## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S76 | 佳里一SS | 11 | 11kV | 1BUS | #1BUS |  | V_R |  |  | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #1 11KV R相電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S76_D1 | [8 empty] | 佳一SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 2ABUS | #2ABUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #2A 11KV R相電壓 |  |  | kV_-9_9(-2000_2000) | aca | B2/S76_D1 | [8 empty] | 佳一SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 3BUS | #3BUS |  | V_R |  |  | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0098 |  |  | 1-E2 |  |  | #3 11KV R相電壓 |  |  | kV_-9_9(-2000_2000) | ada | B2/S76_D1 | [8 empty] | 佳一SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS |  |  |  |  | CDC | 4 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 4BUS | #4BUS |  | V_R |  |  | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0137 |  |  | 2-89 |  |  | #4 11KV R相電壓 |  |  | kV_-9_9(-2000_2000) | aea | B2/S76_D1 | [8 empty] | 佳一SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS |  |  |  |  | CDC | 5 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 5BUS | #5BUS |  | V_R |  |  | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0173 |  |  | 2-AD |  |  | #5 11KV R相電壓 |  |  | kV_-9_9(-2000_2000) | afa | B2/S76_D1 | [8 empty] | 佳一SS.11KV#5BUS_KV | 11KV #5BUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | BE1 | 69B1E(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 7 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0285 |  |  | 1-31-13 |  |  | 69KV BUS #1 衡相監視 |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 8 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | #620學甲佳里二路 瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S76_A1 | [8 empty] | 佳一SS.620_MW | 學甲佳里二路 MW | LINE69 |  |  |  |  | CDC | 9 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | #620學甲佳里二路 乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S76_A1 | [8 empty] | 佳一SS.620_MVAR | 學甲佳里二路 MVAR | LINE69 |  |  |  |  | CDC | 10 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0040 |  |  | 2-48 |  |  | #620學甲佳里二路 MWH(+) |  |  |  |  | B2/S76_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 11 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | #730學甲佳里一路 瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S76_A1 | [8 empty] | 佳一SS.730_MW | 學甲佳里一路 MW | LINE69 |  |  |  |  | CDC | 12 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | #730學甲佳里一路 乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S76_A1 | [8 empty] | 佳一SS.730_MVAR | 學甲佳里一路 MVAR | LINE69 |  |  |  |  | CDC | 13 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0042 |  |  | 2-4A |  |  | #730學甲佳里一路 MWH(+) |  |  |  |  | B2/S76_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 14 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | #650麻豆佳里線 瓦 |  |  | MW_-144_144(-2000_2000) |  | B2/S76_A1 | [8 empty] | 佳一SS.650_MW | 佳里麻豆線 MW | LINE69 |  |  |  |  | CDC | 15 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | #650麻豆佳里線 乏 |  |  | MVAR_-144_144(-2000_2000) |  | B2/S76_A1 | [8 empty] | 佳一SS.650_MVAR | 佳里麻豆線 MVAR | LINE69 |  |  |  |  | CDC | 16 | AI_LINE69 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0044 |  |  | 2-4C |  |  | #650麻豆佳里線 MWH(+) |  |  |  |  | B2/S76_A1 | [8 empty] | Point Empty | [6 empty] | CDC | 17 | AI_LINE69 | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | #620學甲佳里二路 67 RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.620_PHA | 學甲佳里二路(620) 相間RY | LINE69 |  |  |  |  | CDC | 18 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | #620學甲佳里二路 67N RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.620_GDA | 學甲佳里二路(620) 接地RY | LINE69 |  |  |  |  | CDC | 19 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | #650麻豆佳里線 67 RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.650_PHA | 佳里麻豆線(650) 相間RY | LINE69 |  |  |  |  | CDC | 20 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | #650麻豆佳里線 67N RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.650_GDA | 佳里麻豆線(650) 接地RY | LINE69 |  |  |  |  | CDC | 21 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | #730學甲佳里一路 67 RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.730_PHA | 學甲佳里一路(730) 相間RY | LINE69 |  |  |  |  | CDC | 22 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | #730學甲佳里一路 67N RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.730_GDA | 學甲佳里一路(730) 接地RY | LINE69 |  |  |  |  | CDC | 23 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | 87A |  | B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | #730學甲佳里一路 87 RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.730_87A | 730學甲佳里一路87RY | OTHER |  |  |  |  | CDC | 24 | DI_LINE69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/S43S762/T2 |  | 0128 |  | 0001 | 1-10-00 |  | 1-01 | #620學甲佳里二路 CB |  |  |  | aaaa | B2/S76_A1 | [8 empty] | 佳一SS.620_CB | 620(學甲佳里二路) CB | LINE69 |  |  |  |  | CDC | 25 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/S43S761/T1 |  | 0132 |  | 0002 | 1-10-04 |  | 1-02 | #650麻豆佳里線 CB |  |  |  | aaca | B2/S76_A1 | [8 empty] | 佳一SS.650_CB | 650(佳里麻豆線) CB | LINE69 |  |  |  |  | CDC | 26 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbE | B/1BUS | B/2BUS | L/S42S76/T2 |  | 0136 |  | 0003 | 1-11-00 |  | 1-03 | #730學甲佳里一路 CB |  |  |  | aaea | B2/S76_A1 | [8 empty] | 佳一SS.730_CB | 730(學甲佳里一路) CB | LINE69 |  |  |  |  | CDC | 27 | DI_LINE69(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | LE0 | 620LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 28 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | LE0 | 730LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.730LE | 730LE (非取樣點) | LINE69 | [5 empty] | 29 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | LE0 | 650LE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.650LE | 650LE (非取樣點) | LINE69 | [5 empty] | 30 | DI_LINE69(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 佳25線 (F5) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳25線KVAR | 11KV佳25線 KVAR | FEEDER |  |  |  |  | CDC | 31 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 佳25線 (F5) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳25線A1 | 11KV佳25線 R相AMP | FEEDER |  |  |  |  | CDC | 32 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 佳25線 (F5) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳25線A2 | 11KV佳25線 S相AMP | FEEDER |  |  |  |  | CDC | 33 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 佳25線 (F5) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳25線A3 | 11KV佳25線 T相AMP | FEEDER |  |  |  |  | CDC | 34 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 佳25線 (F5) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳25線A0 | 11KV佳25線 N相AMP | FEEDER |  |  |  |  | CDC | 35 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 佳25線 (F5) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 36 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 佳30線 (F10) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳30線KVAR | 11KV佳30線 KVAR | FEEDER |  |  |  |  | CDC | 37 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 佳30線 (F10) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳30線A1 | 11KV佳30線 R相AMP | FEEDER |  |  |  |  | CDC | 38 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 佳30線 (F10) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳30線A2 | 11KV佳30線 S相AMP | FEEDER |  |  |  |  | CDC | 39 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 佳30線 (F10) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳30線A3 | 11KV佳30線 T相AMP | FEEDER |  |  |  |  | CDC | 40 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 佳30線 (F10) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳30線A0 | 11KV佳30線 N相AMP | FEEDER |  |  |  |  | CDC | 41 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | 佳30線 (F10) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 42 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 佳45線 (F21) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳45線KVAR | 11KV佳45線 KVAR | FEEDER |  |  |  |  | CDC | 43 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 佳45線 (F21) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳45線A1 | 11KV佳45線 R相AMP | FEEDER |  |  |  |  | CDC | 44 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 佳45線 (F21) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳45線A2 | 11KV佳45線 S相AMP | FEEDER |  |  |  |  | CDC | 45 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 佳45線 (F21) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳45線A3 | 11KV佳45線 T相AMP | FEEDER |  |  |  |  | CDC | 46 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 佳45線 (F21) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳45線A0 | 11KV佳45線 N相AMP | FEEDER |  |  |  |  | CDC | 47 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0020 |  |  | 1-54 |  |  | 佳45線 (F21) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 48 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | 漚汪線 (F1) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN21_PHA | 11KV漚汪線(KN21) 相間RY | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 漚汪線 (F1) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN21_GDA | 11KV漚汪線(KN21) 接地RY | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | 漚汪線 (F1) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN21_79UL | 11KV漚汪線(KN21) 79RY U/L | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0832 |  | 0152 | 2-34-00 |  | 2-18 | 漚汪線 (F1) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN21_ADJ | 11KV漚汪線(KN21) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 佳興線 (F2) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN22_PHA | 11KV佳興線(KN22) 相間RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 佳興線 (F2) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN22_GDA | 11KV佳興線(KN22) 接地RY | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | 佳興線 (F2) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN22_79UL | 11KV佳興線(KN22) 79RY U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0833 |  | 0153 | 2-34-01 |  | 2-19 | 佳興線 (F2) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN22_ADJ | 11KV佳興線(KN22) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | 佳工線 (F3) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN23_PHA | 11KV佳工線(KN23) 相間RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | 佳工線 (F3) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN23_GDA | 11KV佳工線(KN23) 接地RY | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | 佳工線 (F3) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN23_79UL | 11KV佳工線(KN23) 79RY U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0834 |  | 0154 | 2-34-02 |  | 2-1A | 佳工線 (F3) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN23_ADJ | 11KV佳工線(KN23) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | 通吉線 (F4) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN24_PHA | 11KV通吉線(KN24) 相間RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | 通吉線 (F4) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN24_GDA | 11KV通吉線(KN24) 接地RY | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | 通吉線 (F4) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN24_79UL | 11KV通吉線(KN24) 79RY U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0835 |  | 0155 | 2-34-03 |  | 2-1B | 通吉線 (F4) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN24_ADJ | 11KV通吉線(KN24) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | 佳25線 (F5) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN25_PHA | 11KV佳25線(KN25) 相間RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | 佳25線 (F5) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN25_GDA | 11KV佳25線(KN25) 接地RY | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | 佳25線 (F5) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN25_79UL | 11KV佳25線(KN25) 79RY U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0836 |  | 0156 | 2-34-04 |  | 2-1C | 佳25線 (F5) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN25_ADJ | 11KV佳25線(KN25) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | 漳洲線 (F6) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN26_PHA | 11KV漳洲線(KN26) 相間RY | FEEDER |  |  |  |  | CDC | 69 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | 漳洲線 (F6) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN26_GDA | 11KV漳洲線(KN26) 接地RY | FEEDER |  |  |  |  | CDC | 70 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0081 | 2-30-07 |  | 1-51 | 漳洲線 (F6) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN26_79UL | 11KV漳洲線(KN26) 79RY U/L | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0837 |  | 0157 | 2-34-05 |  | 2-1D | 漳洲線 (F6) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN26_ADJ | 11KV漳洲線(KN26) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 72 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 頂城線 (F7) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN27_PHA | 11KV頂城線(KN27) 相間RY | FEEDER |  |  |  |  | CDC | 73 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 頂城線 (F7) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN27_GDA | 11KV頂城線(KN27) 接地RY | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0082 | 2-30-08 |  | 1-52 | 頂城線 (F7) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN27_79UL | 11KV頂城線(KN27) 79RY U/L | FEEDER |  |  |  |  | CDC | 75 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0838 |  | 0158 | 2-34-06 |  | 2-1E | 頂城線 (F7) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN27_ADJ | 11KV頂城線(KN27) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 76 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 七股線 (F8) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN28_PHA | 11KV七股線(KN28) 相間RY | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | 七股線 (F8) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN28_GDA | 11KV七股線(KN28) 接地RY | FEEDER |  |  |  |  | CDC | 78 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  | 0083 | 2-30-09 |  | 1-53 | 七股線 (F8) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN28_79UL | 11KV七股線(KN28) 79RY U/L | FEEDER |  |  |  |  | CDC | 79 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0839 |  | 0159 | 2-34-07 |  | 2-1F | 七股線 (F8) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN28_ADJ | 11KV七股線(KN28) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 塭寮線 (F9) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN29_PHA | 11KV塭寮線(KN29) 相間RY | FEEDER |  |  |  |  | CDC | 81 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 塭寮線 (F9) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN29_GDA | 11KV塭寮線(KN29) 接地RY | FEEDER |  |  |  |  | CDC | 82 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0084 | 2-30-10 |  | 1-54 | 塭寮線 (F9) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN29_79UL | 11KV塭寮線(KN29) 79RY U/L | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0840 |  | 0160 | 2-34-08 |  | 2-20 | 塭寮線 (F9) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN29_ADJ | 11KV塭寮線(KN29) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 84 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 佳30線 (F10) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN30_PHA | 11KV佳30線(KN30) 相間RY | FEEDER |  |  |  |  | CDC | 85 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 佳30線 (F10) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN30_GDA | 11KV佳30線(KN30) 接地RY | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0085 | 2-30-11 |  | 1-55 | 佳30線 (F10) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN30_79UL | 11KV佳30線(KN30) 79RY U/L | FEEDER |  |  |  |  | CDC | 87 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0841 |  | 0161 | 2-34-09 |  | 2-21 | 佳30線 (F10) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN30_ADJ | 11KV佳30線(KN30) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 88 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 西港線 (F11) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN31_PHA | 11KV西港線(KN31) 相間RY | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 西港線 (F11) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN31_GDA | 11KV西港線(KN31) 接地RY | FEEDER |  |  |  |  | CDC | 90 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0101 | 2-31-07 |  | 1-65 | 西港線 (F11) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN31_79UL | 11KV西港線(KN31) 79RY U/L | FEEDER |  |  |  |  | CDC | 91 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0842 |  | 0162 | 2-34-10 |  | 2-22 | 西港線 (F11) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN31_ADJ | 11KV西港線(KN31) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 子良線 (F12) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN32_PHA | 11KV子良線(KN32) 相間RY | FEEDER |  |  |  |  | CDC | 93 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 子良線 (F12) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN32_GDA | 11KV子良線(KN32) 接地RY | FEEDER |  |  |  |  | CDC | 94 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0102 | 2-31-08 |  | 1-66 | 子良線 (F12) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN32_79UL | 11KV子良線(KN32) 79RY U/L | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0843 |  | 0163 | 2-34-11 |  | 2-23 | 子良線 (F12) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN32_ADJ | 11KV子良線(KN32) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 96 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 嘉福線 (F13) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN33_PHA | 11KV嘉福線(KN33) 相間RY | FEEDER |  |  |  |  | CDC | 97 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 嘉福線 (F13) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN33_GDA | 11KV嘉福線(KN33) 接地RY | FEEDER |  |  |  |  | CDC | 98 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0103 | 2-31-09 |  | 1-67 | 嘉福線 (F13) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN33_79UL | 11KV嘉福線(KN33) 79RY U/L | FEEDER |  |  |  |  | CDC | 99 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0844 |  | 0164 | 2-34-12 |  | 2-24 | 嘉福線 (F13) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN33_ADJ | 11KV嘉福線(KN33) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 100 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 篤加線 (F14) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN34_PHA | 11KV篤加線(KN34) 相間RY | FEEDER |  |  |  |  | CDC | 101 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | 篤加線 (F14) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN34_GDA | 11KV篤加線(KN34) 接地RY | FEEDER |  |  |  |  | CDC | 102 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0104 | 2-31-10 |  | 1-68 | 篤加線 (F14) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN34_79UL | 11KV篤加線(KN34) 79RY U/L | FEEDER |  |  |  |  | CDC | 103 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0845 |  | 0165 | 2-34-13 |  | 2-25 | 篤加線 (F14) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN34_ADJ | 11KV篤加線(KN34) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 104 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 林樂線 (F15) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN35_PHA | 11KV林樂線(KN35) 相間RY | FEEDER |  |  |  |  | CDC | 105 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 林樂線 (F15) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN35_GDA | 11KV林樂線(KN35) 接地RY | FEEDER |  |  |  |  | CDC | 106 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0795 |  | 0105 | 2-31-11 |  | 1-69 | 林樂線 (F15) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN35_79UL | 11KV林樂線(KN35) 79RY U/L | FEEDER |  |  |  |  | CDC | 107 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0846 |  | 0166 | 2-34-14 |  | 2-26 | 林樂線 (F15) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN35_ADJ | 11KV林樂線(KN35) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 108 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | 三股線 (F16) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN36_PHA | 11KV三股線(KN36) 相間RY | FEEDER |  |  |  |  | CDC | 109 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 三股線 (F16) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN36_GDA | 11KV三股線(KN36) 接地RY | FEEDER |  |  |  |  | CDC | 110 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0807 |  | 0121 | 2-32-07 |  | 1-79 | 三股線 (F16) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN36_79UL | 11KV三股線(KN36) 79RY U/L | FEEDER |  |  |  |  | CDC | 111 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0847 |  | 0167 | 2-34-15 |  | 2-27 | 三股線 (F16) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN36_ADJ | 11KV三股線(KN36) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 112 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | 佳塭線 (F17) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN37_PHA | 11KV佳塭線(KN37) 相間RY | FEEDER |  |  |  |  | CDC | 113 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | 佳塭線 (F17) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN37_GDA | 11KV佳塭線(KN37) 接地RY | FEEDER |  |  |  |  | CDC | 114 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0808 |  | 0122 | 2-32-08 |  | 1-7A | 佳塭線 (F17) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN37_79UL | 11KV佳塭線(KN37) 79RY U/L | FEEDER |  |  |  |  | CDC | 115 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0848 |  | 0168 | 2-35-00 |  | 2-28 | 佳塭線 (F17) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN37_ADJ | 11KV佳塭線(KN37) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 116 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | 光復線 (F18) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN38_PHA | 11KV光復線(KN38) 相間RY | FEEDER |  |  |  |  | CDC | 117 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | 光復線 (F18) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN38_GDA | 11KV光復線(KN38) 接地RY | FEEDER |  |  |  |  | CDC | 118 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0809 |  | 0123 | 2-32-09 |  | 1-7B | 光復線 (F18) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN38_79UL | 11KV光復線(KN38) 79RY U/L | FEEDER |  |  |  |  | CDC | 119 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0849 |  | 0169 | 2-35-01 |  | 2-29 | 光復線 (F18) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN38_ADJ | 11KV光復線(KN38) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 120 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 新生線 (F19) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN39_PHA | 11KV新生線(KN39) 相間RY | FEEDER |  |  |  |  | CDC | 121 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 新生線 (F19) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN39_GDA | 11KV新生線(KN39) 接地RY | FEEDER |  |  |  |  | CDC | 122 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0810 |  | 0124 | 2-32-10 |  | 1-7C | 新生線 (F19) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN39_79UL | 11KV新生線(KN39) 79RY U/L | FEEDER |  |  |  |  | CDC | 123 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0850 |  | 0170 | 2-35-02 |  | 2-2A | 新生線 (F19) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN39_ADJ | 11KV新生線(KN39) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 124 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | 仁愛線 (F20) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN40_PHA | 11KV仁愛線(KN40) 相間RY | FEEDER |  |  |  |  | CDC | 125 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0245 |  |  | 1-1E-05 |  |  | 仁愛線 (F20) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN40_GDA | 11KV仁愛線(KN40) 接地RY | FEEDER |  |  |  |  | CDC | 126 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0811 |  | 0125 | 2-32-11 |  | 1-7D | 仁愛線 (F20) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN40_79UL | 11KV仁愛線(KN40) 79RY U/L | FEEDER |  |  |  |  | CDC | 127 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0851 |  | 0171 | 2-35-03 |  | 2-2B | 仁愛線 (F20) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN40_ADJ | 11KV仁愛線(KN40) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 128 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0641 |  |  | 2-10-01 |  |  | 佳45線 (F21) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN45_PHA | 11KV佳45線(KN45) 相間RY | FEEDER |  |  |  |  | CDC | 129 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0642 |  |  | 2-10-02 |  |  | 佳45線 (F21) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN45_GDA | 11KV佳45線(KN45) 接地RY | FEEDER |  |  |  |  | CDC | 130 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0823 |  | 0140 | 2-33-07 |  | 2-0C | 佳45線 (F21) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN45_79UL | 11KV佳45線(KN45) 79RY U/L | FEEDER |  |  |  |  | CDC | 131 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0852 |  | 0172 | 2-35-04 |  | 2-2C | 佳45線 (F21) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN45_ADJ | 11KV佳45線(KN45) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 132 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0643 |  |  | 2-10-03 |  |  | 北農線 (F22) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN41_PHA | 11KV北農線(KN41) 相間RY | FEEDER |  |  |  |  | CDC | 133 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0644 |  |  | 2-10-04 |  |  | 北農線 (F22) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN41_GDA | 11KV北農線(KN41) 接地RY | FEEDER |  |  |  |  | CDC | 134 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0824 |  | 0141 | 2-33-08 |  | 2-0D | 北農線 (F22) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN41_79UL | 11KV北農線(KN41) 79RY U/L | FEEDER |  |  |  |  | CDC | 135 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0853 |  | 0173 | 2-35-05 |  | 2-2D | 北農線 (F22) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN41_ADJ | 11KV北農線(KN41) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 136 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0645 |  |  | 2-10-05 |  |  | 中山線 (F23) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN42_PHA | 11KV中山線(KN42) 相間RY | FEEDER |  |  |  |  | CDC | 137 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0646 |  |  | 2-10-06 |  |  | 中山線 (F23) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN42_GDA | 11KV中山線(KN42) 接地RY | FEEDER |  |  |  |  | CDC | 138 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0825 |  | 0142 | 2-33-09 |  | 2-0E | 中山線 (F23) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN42_79UL | 11KV中山線(KN42) 79RY U/L | FEEDER |  |  |  |  | CDC | 139 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0854 |  | 0174 | 2-35-06 |  | 2-2E | 中山線 (F23) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN42_ADJ | 11KV中山線(KN42) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 140 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0647 |  |  | 2-10-07 |  |  | 佳麻線 (F24) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN43_PHA | 11KV佳麻線(KN43) 相間RY | FEEDER |  |  |  |  | CDC | 141 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0648 |  |  | 2-11-00 |  |  | 佳麻線 (F24) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN43_GDA | 11KV佳麻線(KN43) 接地RY | FEEDER |  |  |  |  | CDC | 142 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0826 |  | 0143 | 2-33-10 |  | 2-0F | 佳麻線 (F24) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN43_79UL | 11KV佳麻線(KN43) 79RY U/L | FEEDER |  |  |  |  | CDC | 143 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0855 |  | 0175 | 2-35-07 |  | 2-2F | 佳麻線 (F24) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN43_ADJ | 11KV佳麻線(KN43) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 144 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0649 |  |  | 2-11-01 |  |  | 佳西線 (F25) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN44_PHA | 11KV佳西線(KN44) 相間RY | FEEDER |  |  |  |  | CDC | 145 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0650 |  |  | 2-11-02 |  |  | 佳西線 (F25) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN44_GDA | 11KV佳西線(KN44) 接地RY | FEEDER |  |  |  |  | CDC | 146 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0827 |  | 0144 | 2-33-11 |  | 2-10 | 佳西線 (F25) 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN44_79UL | 11KV佳西線(KN44) 79RY U/L | FEEDER |  |  |  |  | CDC | 147 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0856 |  | 0176 | 2-35-08 |  | 2-30 | 佳西線 (F25) LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN44_ADJ | 11KV佳西線(KN44) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 148 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KN21/T1 |  |  | 0160 |  | 0052 | 1-14-00 |  | 1-34 | 漚汪線 (F1) CB |  |  |  | aacb | B2/S76_D1 | [8 empty] | 佳一SS.KN21_CB | KN21(11KV漚汪線) CB | FEEDER |  |  |  |  | CDC | 149 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | ES | KN21_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN21_ES | KN21_ES (非取樣點) | FEEDER | [5 empty] | 150 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KN22/T1 |  |  | 0161 |  | 0053 | 1-14-01 |  | 1-35 | 佳興線 (F2) CB |  |  |  | aadb | B2/S76_D1 | [8 empty] | 佳一SS.KN22_CB | KN22(11KV佳興線) CB | FEEDER |  |  |  |  | CDC | 151 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | ES | KN22_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN22_ES | KN22_ES (非取樣點) | FEEDER | [5 empty] | 152 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KN23/T1 |  |  | 0162 |  | 0054 | 1-14-02 |  | 1-36 | 佳工線 (F3) CB |  |  |  | aaeb | B2/S76_D1 | [8 empty] | 佳一SS.KN23_CB | KN23(11KV佳工線) CB | FEEDER |  |  |  |  | CDC | 153 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | ES | KN23_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN23_ES | KN23_ES (非取樣點) | FEEDER | [5 empty] | 154 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KN24/T1 |  |  | 0163 |  | 0055 | 1-14-03 |  | 1-37 | 通吉線 (F4) CB |  |  |  | aafb | B2/S76_D1 | [8 empty] | 佳一SS.KN24_CB | KN24(11KV通吉線) CB | FEEDER |  |  |  |  | CDC | 155 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | ES | KN24_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN24_ES | KN24_ES (非取樣點) | FEEDER | [5 empty] | 156 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KN25/T1 |  |  | 0164 |  | 0056 | 1-14-04 |  | 1-38 | 佳25線 (F5) CB |  |  |  | aahb | B2/S76_D1 | [8 empty] | 佳一SS.KN25_CB | KN25(11KV佳25線) CB | FEEDER |  |  |  |  | CDC | 157 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | L/KN26/T1 |  |  | 0182 |  | 0073 | 1-16-06 |  | 1-49 | 漳洲線 (F6) CB |  |  |  | acbb | B2/S76_D1 | [8 empty] | 佳一SS.KN26_CB | KN26(11KV漳洲線) CB | FEEDER |  |  |  |  | CDC | 158 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | ES | KN26_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN26_ES | KN26_ES (非取樣點) | FEEDER | [5 empty] | 159 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | L/KN27/T1 |  |  | 0183 |  | 0074 | 1-16-07 |  | 1-4A | 頂城線 (F7) CB |  |  |  | accb | B2/S76_D1 | [8 empty] | 佳一SS.KN27_CB | KN27(11KV頂城線) CB | FEEDER |  |  |  |  | CDC | 160 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | ES | KN27_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN27_ES | KN27_ES (非取樣點) | FEEDER | [5 empty] | 161 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | L/KN28/T1 |  |  | 0184 |  | 0075 | 1-17-00 |  | 1-4B | 七股線 (F8) CB |  |  |  | acdb | B2/S76_D1 | [8 empty] | 佳一SS.KN28_CB | KN28(11KV七股線) CB | FEEDER |  |  |  |  | CDC | 162 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | ES | KN28_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN28_ES | KN28_ES (非取樣點) | FEEDER | [5 empty] | 163 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | L/KN29/T1 |  |  | 0185 |  | 0076 | 1-17-01 |  | 1-4C | 塭寮線 (F9) CB |  |  |  | abfb | B2/S76_D1 | [8 empty] | 佳一SS.KN29_CB | KN29(11KV塭寮線) CB | FEEDER |  |  |  |  | CDC | 164 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | ES | KN29_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN29_ES | KN29_ES (非取樣點) | FEEDER | [5 empty] | 165 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | L/KN30/T1 |  |  | 0186 |  | 0077 | 1-17-02 |  | 1-4D | 佳30線 (F10) CB |  |  |  | abdb | B2/S76_D1 | [8 empty] | 佳一SS.KN30_CB | KN30(11KV佳30線) CB | FEEDER |  |  |  |  | CDC | 166 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | ES | KN30_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN30_ES | KN30_ES (非取樣點) | FEEDER | [5 empty] | 167 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KN31/T1 |  |  | 0204 |  | 0093 | 1-19-04 |  | 1-5D | 西港線 (F11) CB |  |  |  | adab | B2/S76_D1 | [8 empty] | 佳一SS.KN31_CB | KN31(11KV西港線) CB | FEEDER |  |  |  |  | CDC | 168 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN31_DS | KN31_DS (非取樣點) | FEEDER | [5 empty] | 169 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | ES | KN31_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN31_ES | KN31_ES (非取樣點) | FEEDER | [5 empty] | 170 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KN32/T1 |  |  | 0205 |  | 0094 | 1-19-05 |  | 1-5E | 子良線 (F12) CB |  |  |  | adbb | B2/S76_D1 | [8 empty] | 佳一SS.KN32_CB | KN32(11KV子良線) CB | FEEDER |  |  |  |  | CDC | 171 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN32_DS | KN32_DS (非取樣點) | FEEDER | [5 empty] | 172 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | ES | KN32_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN32_ES | KN32_ES (非取樣點) | FEEDER | [5 empty] | 173 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KN33/T1 |  |  | 0206 |  | 0095 | 1-19-06 |  | 1-5F | 嘉福線 (F13) CB |  |  |  | adcb | B2/S76_D1 | [8 empty] | 佳一SS.KN33_CB | KN33(11KV嘉福線) CB | FEEDER |  |  |  |  | CDC | 174 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN33_DS | KN33_DS (非取樣點) | FEEDER | [5 empty] | 175 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | ES | KN33_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN33_ES | KN33_ES (非取樣點) | FEEDER | [5 empty] | 176 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KN34/T1 |  |  | 0207 |  | 0096 | 1-19-07 |  | 1-60 | 篤加線 (F14) CB |  |  |  | adeb | B2/S76_D1 | [8 empty] | 佳一SS.KN34_CB | KN34(11KV篤加線) CB | FEEDER |  |  |  |  | CDC | 177 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN34_DS | KN34_DS (非取樣點) | FEEDER | [5 empty] | 178 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | ES | KN34_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN34_ES | KN34_ES (非取樣點) | FEEDER | [5 empty] | 179 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | L/KN35/T1 |  |  | 0208 |  | 0097 | 1-1A-00 |  | 1-61 | 林樂線 (F15) CB |  |  |  | adfb | B2/S76_D1 | [8 empty] | 佳一SS.KN35_CB | KN35(11KV林樂線) CB | FEEDER |  |  |  |  | CDC | 180 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN35_DS | KN35_DS (非取樣點) | FEEDER | [5 empty] | 181 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | ES | KN35_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN35_ES | KN35_ES (非取樣點) | FEEDER | [5 empty] | 182 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KN36/T1 |  |  | 0227 |  | 0113 | 1-1C-03 |  | 1-71 | 三股線 (F16) CB |  |  |  | aeab | B2/S76_D1 | [8 empty] | 佳一SS.KN36_CB | KN36(11KV三股線) CB | FEEDER |  |  |  |  | CDC | 183 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN36_DS | KN36_DS (非取樣點) | FEEDER | [5 empty] | 184 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | ES | KN36_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN36_ES | KN36_ES (非取樣點) | FEEDER | [5 empty] | 185 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KN37/T1 |  |  | 0228 |  | 0114 | 1-1C-04 |  | 1-72 | 佳塭線 (F17) CB |  |  |  | aebb | B2/S76_D1 | [8 empty] | 佳一SS.KN37_CB | KN37(11KV佳塭線) CB | FEEDER |  |  |  |  | CDC | 186 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN37_DS | KN37_DS (非取樣點) | FEEDER | [5 empty] | 187 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | ES | KN37_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN37_ES | KN37_ES (非取樣點) | FEEDER | [5 empty] | 188 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KN38/T1 |  |  | 0229 |  | 0115 | 1-1C-05 |  | 1-73 | 光復線 (F18) CB |  |  |  | aecb | B2/S76_D1 | [8 empty] | 佳一SS.KN38_CB | KN38(11KV光復線) CB | FEEDER |  |  |  |  | CDC | 189 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN38_DS | KN38_DS (非取樣點) | FEEDER | [5 empty] | 190 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | ES | KN38_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN38_ES | KN38_ES (非取樣點) | FEEDER | [5 empty] | 191 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KN39/T1 |  |  | 0230 |  | 0116 | 1-1C-06 |  | 1-74 | 新生線 (F19) CB |  |  |  | aeeb | B2/S76_D1 | [8 empty] | 佳一SS.KN39_CB | KN39(11KV新生線) CB | FEEDER |  |  |  |  | CDC | 192 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN39_DS | KN39_DS (非取樣點) | FEEDER | [5 empty] | 193 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | ES | KN39_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN39_ES | KN39_ES (非取樣點) | FEEDER | [5 empty] | 194 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | L/KN40/T1 |  |  | 0231 |  | 0117 | 1-1C-07 |  | 1-75 | 仁愛線 (F20) CB |  |  |  | aefb | B2/S76_D1 | [8 empty] | 佳一SS.KN40_CB | KN40(11KV仁愛線) CB | FEEDER |  |  |  |  | CDC | 195 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN40_DS | KN40_DS (非取樣點) | FEEDER | [5 empty] | 196 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | ES | KN40_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN40_ES | KN40_ES (非取樣點) | FEEDER | [5 empty] | 197 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/5BUS | L/KN45/T1 |  |  | 0249 |  | 0132 | 1-1F-01 |  | 2-04 | 佳45線 (F21) CB |  |  |  | afab | B2/S76_D1 | [8 empty] | 佳一SS.KN45_CB | KN45(11KV佳45線) CB | FEEDER |  |  |  |  | CDC | 198 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN45_DS | KN45_DS (非取樣點) | FEEDER | [5 empty] | 199 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | ES | KN45_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN45_ES | KN45_ES (非取樣點) | FEEDER | [5 empty] | 200 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/5BUS | L/KN41/T1 |  |  | 0250 |  | 0133 | 1-1F-02 |  | 2-05 | 北農線 (F22) CB |  |  |  | afbb | B2/S76_D1 | [8 empty] | 佳一SS.KN41_CB | KN41(11KV北農線) CB | FEEDER |  |  |  |  | CDC | 201 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN41_DS | KN41_DS (非取樣點) | FEEDER | [5 empty] | 202 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | ES | KN41_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN41_ES | KN41_ES (非取樣點) | FEEDER | [5 empty] | 203 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/5BUS | L/KN42/T1 |  |  | 0251 |  | 0134 | 1-1F-03 |  | 2-06 | 中山線 (F23) CB |  |  |  | afcb | B2/S76_D1 | [8 empty] | 佳一SS.KN42_CB | KN42(11KV中山線) CB | FEEDER |  |  |  |  | CDC | 204 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN42_DS | KN42_DS (非取樣點) | FEEDER | [5 empty] | 205 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | ES | KN42_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN42_ES | KN42_ES (非取樣點) | FEEDER | [5 empty] | 206 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/5BUS | L/KN43/T1 |  |  | 0252 |  | 0135 | 1-1F-04 |  | 2-07 | 佳麻線 (F24) CB |  |  |  | afeb | B2/S76_D1 | [8 empty] | 佳一SS.KN43_CB | KN43(11KV佳麻線) CB | FEEDER |  |  |  |  | CDC | 207 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN43_DS | KN43_DS (非取樣點) | FEEDER | [5 empty] | 208 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | ES | KN43_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN43_ES | KN43_ES (非取樣點) | FEEDER | [5 empty] | 209 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/5BUS | L/KN44/T1 |  |  | 0253 |  | 0136 | 1-1F-05 |  | 2-08 | 佳西線 (F25) CB |  |  |  | affb | B2/S76_D1 | [8 empty] | 佳一SS.KN44_CB | KN44(11KV佳西線) CB | FEEDER |  |  |  |  | CDC | 210 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN44_DS | KN44_DS (非取樣點) | FEEDER | [5 empty] | 211 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | ES | KN44_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN44_ES | KN44_ES (非取樣點) | FEEDER | [5 empty] | 212 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_R | #2MB-#1 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #1-#2 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE1_A1 | 11KV #2B-#1 TIE R相AMP | TIE |  |  |  |  | CDC | 213 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_S | #2MB-#1 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #1-#2 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE1_A2 | 11KV #2B-#1 TIE S相AMP | TIE |  |  |  |  | CDC | 214 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | I_T | #2MB-#1 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #1-#2 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE1_A3 | 11KV #2B-#1 TIE T相AMP | TIE |  |  |  |  | CDC | 215 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_R | #3-#2MA | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #3-#2A TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE2_A1 | 11KV #3-#2A TIE R相AMP | TIE |  |  |  |  | CDC | 216 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_S | #3-#2MA | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | #3-#2A TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE2_A2 | 11KV #3-#2A TIE S相AMP | TIE |  |  |  |  | CDC | 217 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | I_T | #3-#2MA | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | #3-#2A TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE2_A3 | 11KV #3-#2A TIE T相AMP | TIE |  |  |  |  | CDC | 218 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | #3 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE |  |  |  |  | CDC | 219 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | #3 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE |  |  |  |  | CDC | 220 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | #3 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE |  |  |  |  | CDC | 221 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_R | #4-#5 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | #4-#5 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE4_A1 | 11KV #4-#5 TIE R相AMP | TIE |  |  |  |  | CDC | 222 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_S | #4-#5 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | #4-#5 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE4_A2 | 11KV #4-#5 TIE S相AMP | TIE |  |  |  |  | CDC | 223 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | I_T | #4-#5 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | #4-#5 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE4_A3 | 11KV #4-#5 TIE T相AMP | TIE |  |  |  |  | CDC | 224 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE(TIE5) |  | I_R |  | DELETE | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | #5-#1 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE5_A1 | 11KV TIE5 R相AMP | TIE |  |  |  |  | CDC | 225 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE(TIE5) |  | I_S |  | DELETE | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | #5-#1 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE5_A2 | 11KV TIE5 S相AMP | TIE |  |  |  |  | CDC | 226 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE(TIE5) |  | I_T |  | DELETE | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | #5-#1 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.11KV_TIE5_A3 | 11KV TIE5 T相AMP | TIE |  |  |  |  | CDC | 227 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | CB | #2MB-#1 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2A | B/1BUS | B/2ABUS |  |  | 0165 |  | 0050 | 1-14-05 |  | 1-32 | #1- #2 TIE CB |  |  |  | zzzz | B2/S76_D1 | [8 empty] | 佳一SS.TIE1_CB | 11KV #2B-#1 TIE CB | TIE |  |  |  |  | CDC | 228 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51A | #2MB-#1 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | #1- #2 TIE 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE1_51A | 11KV #2B-#1 TIE 51RY | TIE |  |  |  |  | CDC | 229 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | 51NA | #2MB-#1 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | #1- #2 TIE 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE1_51NA | 11KV #2B-#1 TIE 51N RY | TIE |  |  |  |  | CDC | 230 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | CB | #3-#2MA |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/2ABUS | B/3BUS |  |  | 0187 |  | 0071 | 1-17-03 |  | 1-47 | #3- #2A TIE CB |  |  |  | zzzz | B2/S76_D1 | [8 empty] | 佳一SS.TIE2_CB | 11KV #3-#2A TIE CB | TIE |  |  |  |  | CDC | 231 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51A | #3-#2MA |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #3- #2A TIE 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE2_51A | 11KV #3-#2A TIE 51RY | TIE |  |  |  |  | CDC | 232 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | 51NA | #3-#2MA |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | #3- #2A TIE 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE2_51NA | 11KV #3-#2A TIE 51N RY | TIE |  |  |  |  | CDC | 233 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | 型式不明 |  |  |  |  | 0209 |  | 0091 | 1-1A-01 |  | 1-5B | #3 TIE CB |  |  |  | zzzz | B2/S76_D1 | [8 empty] | 佳一SS.TIE3_CB | 11KV TIE3 CB | TIE |  |  |  |  | CDC | 234 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | #3 TIE 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE3_51A | 11KV TIE3 51RY | TIE |  |  |  |  | CDC | 235 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | #3 TIE 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE3_51NA | 11KV TIE3 51N RY | TIE |  |  |  |  | CDC | 236 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | CB | #4-#5 |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/4BUS | B/5BUS |  |  | 0232 |  | 0111 | 1-1D-00 |  | 1-6F | #4- #5 TIE CB |  |  |  | zzzz | B2/S76_D1 | [8 empty] | 佳一SS.TIE4_CB | 11KV #4-#5 TIE CB | TIE |  |  |  |  | CDC | 237 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | 51A | #4-#5 |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | #4- #5 TIE 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE4_51A | 11KV #4-#5 TIE 51RY | TIE |  |  |  |  | CDC | 238 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | 51NA | #4-#5 |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | #4- #5 TIE 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE4_51NA | 11KV #4-#5 TIE 51N RY | TIE |  |  |  |  | CDC | 239 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE(TIE5) |  | CB |  | DELETE | Status | CB | Close/Open | Y | 1 | DI-SP |  | 型式不明 |  |  |  |  | 0651 |  | 0146 | 2-11-03 |  | 2-12 | #5- #1 TIE CB |  |  |  | zzzz | B2/S76_D1 | [8 empty] | 佳一SS.TIE5_CB | 11KV TIE5 CB | TIE |  |  |  |  | CDC | 240 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE(TIE5) |  | 51A |  | DELETE | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0652 |  |  | 2-11-04 |  |  | #5- #1 TIE 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE5_51A | 11KV TIE5 51RY | TIE |  |  |  |  | CDC | 241 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE(TIE5) |  | 51NA |  | DELETE | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0653 |  |  | 2-11-05 |  |  | #5- #1 TIE 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.TIE5_51NA | 11KV TIE5 51N RY | TIE |  |  |  |  | CDC | 242 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D1 | #2MB-#1(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.TIE1_DS | #2B-#1 TIE_DS (非取樣點) | TIE | [5 empty] | 243 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | TIE2 | TIE(TIE2) |  | D1 | #3-#2MA(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.TIE2_DS | #3-#2A TIE_DS (非取樣點) | TIE | [5 empty] | 244 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE(TIE3) |  | DS | TIE3(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | [5 empty] | 245 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | TIE4 | TIE(TIE4) |  | D1 | #4-#5(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.TIE4_DS | #4-#5 TIE_DS (非取樣點) | TIE | [5 empty] | 246 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE(TIE5) |  | DS | TIE5(非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.TIE5_DS | TIE5_DS (非取樣點) | TIE | [5 empty] | 247 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #1 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#1MTR_MW | #1MTR二次側 MW | DTR |  |  |  |  | CDC | 248 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #1 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR |  |  |  |  | CDC | 249 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #1 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 250 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #1 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 251 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #1 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 252 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #2 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#2MTR_MW | #2MTR二次側 MW | DTR |  |  |  |  | CDC | 253 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #2 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR |  |  |  |  | CDC | 254 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 255 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 256 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #2 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 257 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#3MTR_MW | #3MTR二次側 MW | DTR |  |  |  |  | CDC | 258 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR |  |  |  |  | CDC | 259 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 260 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #3 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 261 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #3 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 262 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | #4 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#4MTR_MW | #4MTR二次側 MW | DTR |  |  |  |  | CDC | 263 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | #4 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR |  |  |  |  | CDC | 264 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | #4 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 265 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | #4 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 266 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | #4 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 267 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | #5 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#5MTR_MW | #5MTR二次側 MW | DTR |  |  |  |  | CDC | 268 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | #5 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#5MTR_MVAR | #5MTR二次側 MVAR | DTR |  |  |  |  | CDC | 269 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | #5 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#5MTR_A1 | #5MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 270 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | #5 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#5MTR_A2 | #5MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 271 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | #5 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.#5MTR_A3 | #5MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 272 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #1 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_OIL | #1MTR 油溫 | DTR |  |  |  |  | CDC | 273 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_COIL | #1MTR 線溫 | DTR |  |  |  |  | CDC | 274 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #1 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_TAP | #1MTR OLTC TAP | DTR |  |  |  |  | CDC | 275 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.5 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.500000
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0025 |  |  | 1-59 |  |  | #1 TR MWH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 276 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | MVARH_P |  | Element | [12 empty] | 0026 |  |  | 1-5A |  |  | #1 TR MVARH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 277 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #2 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_OIL | #2MTR 油溫 | DTR |  |  |  |  | CDC | 278 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #2 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_COIL | #2MTR 線溫 | DTR |  |  |  |  | CDC | 279 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #2 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_TAP | #2MTR OLTC TAP | DTR |  |  |  |  | CDC | 280 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0028 |  |  | 1-5C |  |  | #2 TR MWH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 281 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | MVARH_P |  | Element | [12 empty] | 0029 |  |  | 1-5D |  |  | #2 TR MVARH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 282 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | #3 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_OIL | #3MTR 油溫 | DTR |  |  |  |  | CDC | 283 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | #3 TR 線溫 |  |  | COIL_-150_150(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_COIL | #3MTR 線溫 | DTR |  |  |  |  | CDC | 284 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0101 |  | 0098 | 1-E5 |  | 1-62 | #3 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_TAP | #3MTR OLTC TAP | DTR |  |  |  |  | CDC | 285 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0031 |  |  | 1-5F |  |  | #3 TR MWH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 286 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | MVARH_P |  | Element | [12 empty] | 0032 |  |  | 2-40 |  |  | #3 TR MVARH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 287 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | #4 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_OIL | #4MTR 油溫 | DTR |  |  |  |  | CDC | 288 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | #4 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_COIL | #4MTR 線溫 | DTR |  |  |  |  | CDC | 289 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0140 |  | 0118 | 2-8C |  | 1-76 | #4 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_TAP | #4MTR OLTC TAP | DTR |  |  |  |  | CDC | 290 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0034 |  |  | 2-42 |  |  | #4 TR MWH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 291 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | MVARH_P |  | Element | [12 empty] | 0035 |  |  | 2-43 |  |  | #4 TR MVARH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 292 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | #5 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_OIL | #5MTR 油溫 | DTR |  |  |  |  | CDC | 293 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | #5 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_COIL | #5MTR 線溫 | DTR |  |  |  |  | CDC | 294 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0176 |  | 0137 | 2-B0 |  | 2-09 | #5 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_TAP | #5MTR OLTC TAP | DTR |  |  |  |  | CDC | 295 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0037 |  |  | 2-45 |  |  | #5 TR MWH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 296 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | MVARH_P |  | Element | [12 empty] | 0038 |  |  | 2-46 |  |  | #5 TR MVARH(+) |  |  |  |  | B1/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 297 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/1MTR |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | #1TR 一次 (750) CB |  |  |  | aabb | B3/S76_D1 | [8 empty] | 佳一SS.750_CB | 750(#1MTR) CB | DTR |  |  |  |  | CDC | 298 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/2MTR |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | #2TR 一次 (760) CB |  |  |  | aafb | B3/S76_D1 | [8 empty] | 佳一SS.760_CB | 760(#2MTR) CB | DTR |  |  |  |  | CDC | 299 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/3MTR |  | 0022 |  | 0088 | 1-02-06 |  | 1-58 | #3TR 一次 (770) CB |  |  |  | aahb | B3/S76_D1 | [8 empty] | 佳一SS.770_CB | 770(#3MTR) CB | DTR |  |  |  |  | CDC | 300 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/4MTR |  | 0034 |  | 0108 | 1-04-02 |  | 1-6C | #4TR 一次 (780) CB |  |  |  | aaib | B3/S76_D1 | [8 empty] | 佳一SS.780_CB | 780(#4MTR) CB | DTR |  |  |  |  | CDC | 301 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/5MTR |  | 0046 |  | 0128 | 1-05-06 |  | 2-00 | #5TR 一次 (790) CB |  |  |  | aajb | B3/S76_D1 | [8 empty] | 佳一SS.790_CB | 790(#5MTR) CB | DTR |  |  |  |  | CDC | 302 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #1TR 二次 (#1MT) CB |  |  |  | aaga | B2/S76_D1 | [8 empty] | 佳一SS.1M_CB | 1M(#1MTR) CB | DTR |  |  |  |  | CDC | 303 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | T/2MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | #2TR 二次 (A) CB |  |  |  | abca | B2/S76_D1 | [8 empty] | 佳一SS.2MA_CB | 2MA(#2MTR) CB | DTR |  |  |  |  | CDC | 304 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | T/3MTR |  |  | 0023 |  | 0089 | 1-02-07 |  | 1-59 | #3TR 二次 (A) CB |  |  |  | adda | B2/S76_D1 | [8 empty] | 佳一SS.3M_CB | 3M(#3MTR) CB | DTR |  |  |  |  | CDC | 305 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | T/4MTR |  |  | 0035 |  | 0109 | 1-04-03 |  | 1-6D | #4TR 二次 (A) CB |  |  |  | aeda | B2/S76_D1 | [8 empty] | 佳一SS.4M_CB | 4M(#4MTR) CB | DTR |  |  |  |  | CDC | 306 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/5BUS | T/5MTR |  |  | 0047 |  | 0129 | 1-05-07 |  | 2-01 | #5TR 二次 (A) CB |  |  |  | afda | B2/S76_D1 | [8 empty] | 佳一SS.5M_CB | 5M(#5MTR) CB | DTR |  |  |  |  | CDC | 307 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #1TR 一次 (750) 51 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#1MTR_51A | #1MTR 51RY | DTR |  |  |  |  | CDC | 308 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #1TR 一次 (750) 51N RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#1MTR_51NA | #1MTR 51N RY | DTR |  |  |  |  | CDC | 309 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #1TR 51Z RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_51ZA | #1MTR 51Z RY | DTR |  |  |  |  | CDC | 310 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #1TR 87 RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_87A | #1MTR 87RY | DTR |  |  |  |  | CDC | 311 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #1TR 87 LS1S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_87UL | #1MTR 87RY U/L | DTR |  |  |  |  | CDC | 312 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  | 0065 | 1-14-06 |  | 1-41 | #760 #780 81 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#2MTR_81A/S | #760 #780 81RY A/S | DTR |  |  |  |  | CDC | 313 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #2TR 一次 (760) 51 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#2MTR_51A | #2MTR 51RY | DTR |  |  |  |  | CDC | 314 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #2TR 一次 (760) 51N RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#2MTR_51NA | #2MTR 51N RY | DTR |  |  |  |  | CDC | 315 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #2TR 51Z RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_51ZA | #2MTR 51Z RY | DTR |  |  |  |  | CDC | 316 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #2TR 87 RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_87A | #2MTR 87RY | DTR |  |  |  |  | CDC | 317 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  |  | 2-30-03 |  |  | #2TR 87 LS1S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_87UL | #2MTR 87RY U/L | DTR |  |  |  |  | CDC | 318 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | #3TR 一次 (770) 51 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#3MTR_51A | #3MTR 51RY | DTR |  |  |  |  | CDC | 319 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | #3TR 一次 (770) 51N RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#3MTR_51NA | #3MTR 51N RY | DTR |  |  |  |  | CDC | 320 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #3TR 51Z RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_51ZA | #3MTR 51Z RY | DTR |  |  |  |  | CDC | 321 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | #3TR 87 RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_87A | #3MTR 87RY | DTR |  |  |  |  | CDC | 322 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  |  | 2-31-03 |  |  | #3TR 87 LS1S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_87UL | #3MTR 87RY U/L | DTR |  |  |  |  | CDC | 323 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  | 0106 | 1-1A-02 |  | 1-6A | #770 81 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#3MTR_81A/S | #770 81RY A/S | DTR |  |  |  |  | CDC | 324 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | #4TR 一次 (780) 51 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#4MTR_51A | #4MTR 51RY | DTR |  |  |  |  | CDC | 325 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | #4TR 一次 (780) 51N RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#4MTR_51NA | #4MTR 51N RY | DTR |  |  |  |  | CDC | 326 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #4TR 51Z RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_51ZA | #4MTR 51Z RY | DTR |  |  |  |  | CDC | 327 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | #4TR 87 RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_87A | #4MTR 87RY | DTR |  |  |  |  | CDC | 328 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0803 |  |  | 2-32-03 |  |  | #4TR 87 LS1S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_87UL | #4MTR 87RY U/L | DTR |  |  |  |  | CDC | 329 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #5TR 一次 (790) 51 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#5MTR_51A | #5MTR 51RY | DTR |  |  |  |  | CDC | 330 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #5TR 一次 (790) 51N RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#5MTR_51NA | #5MTR 51N RY | DTR |  |  |  |  | CDC | 331 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #5TR 51Z RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_51ZA | #5MTR 51Z RY | DTR |  |  |  |  | CDC | 332 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #5TR 87 RY |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_87A | #5MTR 87RY | DTR |  |  |  |  | CDC | 333 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 2-33-03 |  |  | #5TR 87 LS1S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_87UL | #5MTR 87RY U/L | DTR |  |  |  |  | CDC | 334 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | 81AS |  | B2,B3 | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  | 0145 | 1-1F-06 |  | 2-11 | #5 BUS 81 RY |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.#5MTR_81A/S | #5MTR 81RY A/S | DTR |  |  |  |  | CDC | 335 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #1TR 二次 (#1MT) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.1M_51A | #1MTR二次側(1M) 51RY | DTR |  |  |  |  | CDC | 336 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0304 |  |  | 1-33-00 |  |  | #1TR 重故障 |  |  |  | a | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_TRA | #1MTR 重故障 | DTR |  |  |  |  | CDC | 337 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #1TR 輕故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_TRF | #1MTR 輕故障 | DTR |  |  |  |  | CDC | 338 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #1TR OLTC R/L |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_S/L | #1MTR OLTC S/L | DTR |  |  |  |  | CDC | 339 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #1TR OLTC A/M |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_A/M | #1MTR OLTC A/M | DTR |  |  |  |  | CDC | 340 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #2TR 二次 (A) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR |  |  |  |  | CDC | 341 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0768 |  |  | 2-30-00 |  |  | #2TR 重故障 |  |  |  | a | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_TRA | #2MTR 重故障 | DTR |  |  |  |  | CDC | 342 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0769 |  |  | 2-30-01 |  |  | #2TR 輕故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_TRF | #2MTR 輕故障 | DTR |  |  |  |  | CDC | 343 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0772 |  |  | 2-30-04 |  |  | #2TR OLTC R/L |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_S/L | #2MTR OLTC S/L | DTR |  |  |  |  | CDC | 344 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0079 | 2-30-05 |  | 1-4F | #2TR OLTC A/M |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_A/M | #2MTR OLTC A/M | DTR |  |  |  |  | CDC | 345 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | #3TR 二次 (A) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.3M_51A | #3MTR二次側(3M) 51RY | DTR |  |  |  |  | CDC | 346 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0784 |  |  | 2-31-00 |  |  | #3TR 重故障 |  |  |  | a | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_TRA | #3MTR 重故障 | DTR |  |  |  |  | CDC | 347 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0785 |  |  | 2-31-01 |  |  | #3TR 輕故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_TRF | #3MTR 輕故障 | DTR |  |  |  |  | CDC | 348 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0788 |  |  | 2-31-04 |  |  | #3TR OLTC R/L |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_S/L | #3MTR OLTC S/L | DTR |  |  |  |  | CDC | 349 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0789 |  | 0099 | 2-31-05 |  | 1-63 | #3TR OLTC A/M |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_A/M | #3MTR OLTC A/M | DTR |  |  |  |  | CDC | 350 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | #4TR 二次 (A) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.4M_51A | #4MTR二次側(4M) 51RY | DTR |  |  |  |  | CDC | 351 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0800 |  |  | 2-32-00 |  |  | #4TR 重故障 |  |  |  | a | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_TRA | #4MTR 重故障 | DTR |  |  |  |  | CDC | 352 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0801 |  |  | 2-32-01 |  |  | #4TR 輕故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_TRF | #4MTR 輕故障 | DTR |  |  |  |  | CDC | 353 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 2-32-04 |  |  | #4TR OLTC R/L |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_S/L | #4MTR OLTC S/L | DTR |  |  |  |  | CDC | 354 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0805 |  | 0119 | 2-32-05 |  | 1-77 | #4TR OLTC A/M |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_A/M | #4MTR OLTC A/M | DTR |  |  |  |  | CDC | 355 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #5TR 二次 (A) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.5M_51A | #5MTR二次側(5M) 51RY | DTR |  |  |  |  | CDC | 356 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0816 |  |  | 2-33-00 |  |  | #5TR 重故障 |  |  |  | a | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_TRA | #5MTR 重故障 | DTR |  |  |  |  | CDC | 357 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | #5TR 輕故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_TRF | #5MTR 輕故障 | DTR |  |  |  |  | CDC | 358 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 2-33-04 |  |  | #5TR OLTC R/L |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_S/L | #5MTR OLTC S/L | DTR |  |  |  |  | CDC | 359 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0821 |  | 0138 | 2-33-05 |  | 2-0A | #5TR OLTC A/M |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_A/M | #5MTR OLTC A/M | DTR |  |  |  |  | CDC | 360 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | DS1 | 1M_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.1M_DS | 1M_DS (非取樣點) | DTR | [5 empty] | 361 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | ES | 1M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.1M_ES | 1M_ES (非取樣點) | DTR | [5 empty] | 362 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 96PA |  | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #1TR 機械保護動作(96PA) |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR |  |  |  |  | CDC | 363 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #1TR OLTC 遲滯 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 364 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #1TR 冷卻電源故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR |  |  |  |  | CDC | 365 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | DS1 | 2M_(非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.2MA_DS | 2MA_DS (非取樣點) | DTR | [5 empty] | 366 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | ES | 2M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.2MA_ES | 2MA_ES (非取樣點) | DTR | [5 empty] | 367 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 96PA |  | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #2TR 機械保護動作(96PA) |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR |  |  |  |  | CDC | 368 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 2-30-02 |  |  | #2TR OLTC 遲滯 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 369 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0780 |  |  | 2-30-12 |  |  | #2TR 冷卻電源故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR |  |  |  |  | CDC | 370 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.3M_DS | 3M_DS (非取樣點) | DTR | [5 empty] | 371 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | ES | 3M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.3M_ES | 3M_ES (非取樣點) | DTR | [5 empty] | 372 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 96PA |  | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | #3TR 機械保護動作(96PA) |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR |  |  |  |  | CDC | 373 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0786 |  |  | 2-31-02 |  |  | #3TR OLTC 遲滯 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 374 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0796 |  |  | 2-31-12 |  |  | #3TR 冷卻電源故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR |  |  |  |  | CDC | 375 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.4M_DS | 4M_DS (非取樣點) | DTR | [5 empty] | 376 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | ES | 4M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.4M_ES | 4M_ES (非取樣點) | DTR | [5 empty] | 377 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 96PA |  | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | #4TR 機械保護動作(96PA) |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_96PA | #4MTR 機械保護動作 | DTR |  |  |  |  | CDC | 378 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0802 |  |  | 2-32-02 |  |  | #4TR OLTC 遲滯 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 379 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-32-12 |  |  | #4TR 冷卻電源故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR |  |  |  |  | CDC | 380 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.5M_DS | 5M_DS (非取樣點) | DTR | [5 empty] | 381 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | ES | 5M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.5M_ES | 5M_ES (非取樣點) | DTR | [5 empty] | 382 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 96PA |  | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #5TR 機械保護動作(96PA) |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_96PA | #5MTR 機械保護動作 | DTR |  |  |  |  | CDC | 383 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | #5TR OLTC 遲滯 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_OLTC遲滯 | #5MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 384 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 2-33-12 |  |  | #5TR 冷卻電源故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_AC_FAULT | #5MTR AC電源失效 | DTR |  |  |  |  | CDC | 385 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | C/1SC |  | 0156 |  | 0008 | 1-13-04 |  | 1-08 | 69KV (810) SC CB |  |  |  | aadb | B2/S76_A1 | [8 empty] | 佳一SS.810_CB | 810(69KV #1SC) CB | SC |  |  |  |  | CDC | 386 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | ES | 810_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.810CE | 810CE (非取樣點) | SC | [5 empty] | 387 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | C/1SC |  |  | 0159 |  | 0051 | 1-13-07 |  | 1-33 | #1 11KV SC CB |  |  |  | aaab | B2/S76_D1 | [8 empty] | 佳一SS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 388 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #1SC Q-CTL A/M |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.210_A/M | 11KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 389 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.210SCES | 210SCES (非取樣點) | SC | [5 empty] | 390 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2ABUS | C/2SC |  |  | 0181 |  | 0072 | 1-16-05 |  | 1-48 | #2 11KV SC CB |  |  |  | abab | B2/S76_D1 | [8 empty] | 佳一SS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 391 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0774 |  | 0080 | 2-30-06 |  | 1-50 | #2SC Q-CTL A/M |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.220_A/M | 11KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 392 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.220SCES | 220SCES (非取樣點) | SC | [5 empty] | 393 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/3BUS | C/3SC |  |  | 0203 |  | 0092 | 1-19-03 |  | 1-5C | #3 11KV SC CB |  |  |  | adgb | B2/S76_D1 | [8 empty] | 佳一SS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 394 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0790 |  | 0100 | 2-31-06 |  | 1-64 | #3SC Q-CTL A/M |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.230_A/M | 11KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 395 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | ES | 230_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.230SCES | 230SCES (非取樣點) | SC | [5 empty] | 396 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/4BUS | C/4SC |  |  | 0226 |  | 0112 | 1-1C-02 |  | 1-70 | #4 11KV SC CB |  |  |  | aegb | B2/S76_D1 | [8 empty] | 佳一SS.240_CB | 240(11KV #4SC) CB | SC |  |  |  |  | CDC | 397 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0806 |  | 0120 | 2-32-06 |  | 1-78 | #4SC Q-CTL A/M |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.240_A/M | 11KV #4SC 乏控器 A/M | SC |  |  |  |  | CDC | 398 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | ES | 240_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.240SCES | 240SCES (非取樣點) | SC | [5 empty] | 399 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/5BUS | C/5SC |  |  | 0248 |  | 0131 | 1-1F-00 |  | 2-03 | #5 11KV SC CB |  |  |  | afgb | B2/S76_D1 | [8 empty] | 佳一SS.250_CB | 250(11KV #5SC) CB | SC |  |  |  |  | CDC | 400 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0822 |  | 0139 | 2-33-06 |  | 2-0B | #5SC Q-CTL A/M |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.250_A/M | 11KV #5SC 乏控器 A/M | SC |  |  |  |  | CDC | 401 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | ES | 250_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.250SCES | 250SCES (非取樣點) | SC | [5 empty] | 402 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | 69KV (810) SC 51,51N RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.810_SCA | 69KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 403 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0158 |  |  | 1-13-06 |  |  | 69KV (810) SC 27,59 RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.810_OUVA | 69KV #1SC 27,59RY | SC |  |  |  |  | CDC | 404 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | #1SC 51,51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.210_SCA | 11KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 405 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | #1SC 27,59 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 406 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | #2SC 51,51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 407 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | #2SC 27,59 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 408 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | #3SC 51,51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.230_SCA | 11KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 409 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | #3SC 27,59 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 410 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | #4SC 51,51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.240_SCA | 11KV #4SC 51,51N RY | SC |  |  |  |  | CDC | 411 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | #4SC 27,59 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC |  |  |  |  | CDC | 412 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0255 |  |  | 1-1F-07 |  |  | #5SC 51,51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.250_SCA | 11KV #5SC 51,51N RY | SC |  |  |  |  | CDC | 413 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0640 |  |  | 2-10-00 |  |  | #5SC 27,59 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.250_UVA | 11KV #5SC 27RY(欠壓) | SC |  |  |  |  | CDC | 414 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 415 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 416 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 417 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 418 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 419 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 420 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 421 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 422 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 423 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCL3 |  | B2 | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 424 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCH3 |  | B2 | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 425 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCL4 |  | B2 | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 426 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | ADCH4 |  | B2 | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 漚汪線 (F1) 瓦 |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 427 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 佳一SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 428 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 429 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 430 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | #2 充電機 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 431 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | 其他輕故障 |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 432 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | 門禁(保全) |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER |  |  |  |  | CDC | 433 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | 開關場照明 C/T |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 434 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電警報 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 435 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-33-13 |  |  | ACB 1S |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 436 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-33-14 |  |  | ACB 2S |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 437 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 438 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 439 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 440 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 441 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 442 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 443 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 444 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 445 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 2-35-12 |  |  | 通訊設備 AC 故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 446 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0861 |  |  | 2-35-13 |  |  | 通訊設備光纖主故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 447 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0862 |  |  | 2-35-14 |  |  | 通訊設備光纖次故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 448 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0863 |  |  | 2-35-15 |  |  | 博碼調變器故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 449 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | 門禁(小門) |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 450 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場照明A/M | Element | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | 開關場照明 A/M |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 451 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | 變電所低水位 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 452 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | 安全監控 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.安全監控 | 保全設定 | OTHER |  |  |  |  | CDC | 453 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | 60A | 69KVSC警報 | B2,B3,Element | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0280 |  |  | 1-31-08 |  |  | 69KV (810) SC 警報 |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 454 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 455 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #1TR 二次 (#1MT) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#1_MAIN_51NA | #1MCB GDA | OTHER |  |  |  |  | CDC | 456 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2TR 二次 (A) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#2_MA_51NA | #2MA GDA | OTHER |  |  |  |  | CDC | 457 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M3 | #3MTR(M3) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | #3TR 二次 (A) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#3_MAIN_51NA | #3MCB GDA | OTHER |  |  |  |  | CDC | 458 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M4 | #4MTR(M4) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | #4TR 二次 (A) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#4_MAIN_51NA | #4MCB GDA | OTHER |  |  |  |  | CDC | 459 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M5 | #5MTR(M5) |  | 51NA |  | B2,B3,Element | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #5TR 二次 (A) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#5_MAIN_51NA | #5MCB GDA | OTHER |  |  |  |  | CDC | 460 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | 火警 |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.火災警報 | 火警 | OTHER |  |  |  |  | CDC | 461 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 81RY_IED_FA | Element | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 其他重故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 462 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 水氣霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | 水氣霧故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.水氣霧故障 | 水氣霧故障 | OTHER |  |  |  |  | CDC | 463 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 水氣霧警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | 水氣霧警報 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.水氣霧警報 | 水氣霧警報 | OTHER |  |  |  |  | CDC | 464 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0233 |  | 0126 | 1-1D-01 |  | 1-7E | 全所故障指示器復歸點 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 465 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | PMA | PM_CFA | Element | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  | Card7 CH83 |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 466 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | Element | [12 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 467 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 468 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | Water | 變電所高水位 | Element | Status | 地下室淹水 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 變電所高水位 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 469 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 470 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | #620學甲佳里二路 87 RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.620_87A | 學甲佳里二路(620) 87RY | OTHER |  |  |  |  | CDC | 471 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0288 |  | 0009 | 1-32-00 |  | 1-09 | #620學甲佳里二路 87RY U/L |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.620_87UL | 學甲佳里二路(620) 87RY U/L | OTHER |  |  |  |  | CDC | 472 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | #650麻豆佳里線 87 RY |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.650_87A | 650麻豆佳里線87RY | OTHER |  |  |  |  | CDC | 473 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0290 |  | 0010 | 1-32-02 |  | 1-0A | #650麻豆佳里線 87RY U/L |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.650_87UL | 650麻豆佳里線87RY UL | OTHER |  |  |  |  | CDC | 474 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0012 |  |  | 1-8C |  |  | 69KV BUS#1 電壓 |  |  | kV_-90_90(-2000_2000) | aaa | B2/S76_A1 | [8 empty] | 佳一SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | [5 empty] | 475 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 七股線 (F8) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.七股線KVAR | 11KV七股線 KVAR | FEEDER |  |  |  |  | CDC | 476 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 七股線 (F8) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.七股線A1 | 11KV七股線 R相AMP | FEEDER |  |  |  |  | CDC | 477 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 七股線 (F8) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.七股線A2 | 11KV七股線 S相AMP | FEEDER |  |  |  |  | CDC | 478 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 七股線 (F8) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.七股線A3 | 11KV七股線 T相AMP | FEEDER |  |  |  |  | CDC | 479 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 七股線 (F8) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.七股線A0 | 11KV七股線 N相AMP | FEEDER |  |  |  |  | CDC | 480 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 三股線 (F16) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.三股線KVAR | 11KV三股線 KVAR | FEEDER |  |  |  |  | CDC | 481 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 三股線 (F16) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.三股線A1 | 11KV三股線 R相AMP | FEEDER |  |  |  |  | CDC | 482 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 三股線 (F16) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.三股線A2 | 11KV三股線 S相AMP | FEEDER |  |  |  |  | CDC | 483 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 三股線 (F16) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.三股線A3 | 11KV三股線 T相AMP | FEEDER |  |  |  |  | CDC | 484 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 三股線 (F16) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.三股線A0 | 11KV三股線 N相AMP | FEEDER |  |  |  |  | CDC | 485 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 子良線 (F12) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.子良線KVAR | 11KV子良線 KVAR | FEEDER |  |  |  |  | CDC | 486 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 子良線 (F12) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.子良線A1 | 11KV子良線 R相AMP | FEEDER |  |  |  |  | CDC | 487 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 子良線 (F12) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.子良線A2 | 11KV子良線 S相AMP | FEEDER |  |  |  |  | CDC | 488 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 子良線 (F12) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.子良線A3 | 11KV子良線 T相AMP | FEEDER |  |  |  |  | CDC | 489 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 子良線 (F12) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.子良線A0 | 11KV子良線 N相AMP | FEEDER |  |  |  |  | CDC | 490 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | 中山線 (F23) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.中山線KVAR | 11KV中山線 KVAR | FEEDER |  |  |  |  | CDC | 491 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 中山線 (F23) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.中山線A1 | 11KV中山線 R相AMP | FEEDER |  |  |  |  | CDC | 492 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 中山線 (F23) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.中山線A2 | 11KV中山線 S相AMP | FEEDER |  |  |  |  | CDC | 493 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 中山線 (F23) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.中山線A3 | 11KV中山線 T相AMP | FEEDER |  |  |  |  | CDC | 494 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 中山線 (F23) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.中山線A0 | 11KV中山線 N相AMP | FEEDER |  |  |  |  | CDC | 495 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 仁愛線 (F20) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.仁愛線KVAR | 11KV仁愛線 KVAR | FEEDER |  |  |  |  | CDC | 496 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 仁愛線 (F20) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.仁愛線A1 | 11KV仁愛線 R相AMP | FEEDER |  |  |  |  | CDC | 497 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 仁愛線 (F20) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.仁愛線A2 | 11KV仁愛線 S相AMP | FEEDER |  |  |  |  | CDC | 498 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 仁愛線 (F20) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.仁愛線A3 | 11KV仁愛線 T相AMP | FEEDER |  |  |  |  | CDC | 499 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 仁愛線 (F20) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.仁愛線A0 | 11KV仁愛線 N相AMP | FEEDER |  |  |  |  | CDC | 500 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 北農線 (F22) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.北農線KVAR | 11KV北農線 KVAR | FEEDER |  |  |  |  | CDC | 501 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 北農線 (F22) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.北農線A1 | 11KV北農線 R相AMP | FEEDER |  |  |  |  | CDC | 502 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 北農線 (F22) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.北農線A2 | 11KV北農線 S相AMP | FEEDER |  |  |  |  | CDC | 503 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 北農線 (F22) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.北農線A3 | 11KV北農線 T相AMP | FEEDER |  |  |  |  | CDC | 504 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 北農線 (F22) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.北農線A0 | 11KV北農線 N相AMP | FEEDER |  |  |  |  | CDC | 505 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 光復線 (F18) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.光復線KVAR | 11KV光復線 KVAR | FEEDER |  |  |  |  | CDC | 506 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 光復線 (F18) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.光復線A1 | 11KV光復線 R相AMP | FEEDER |  |  |  |  | CDC | 507 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 光復線 (F18) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.光復線A2 | 11KV光復線 S相AMP | FEEDER |  |  |  |  | CDC | 508 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 光復線 (F18) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.光復線A3 | 11KV光復線 T相AMP | FEEDER |  |  |  |  | CDC | 509 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 光復線 (F18) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.光復線A0 | 11KV光復線 N相AMP | FEEDER |  |  |  |  | CDC | 510 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 西港線 (F11) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.西港線KVAR | 11KV西港線 KVAR | FEEDER |  |  |  |  | CDC | 511 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 西港線 (F11) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.西港線A1 | 11KV西港線 R相AMP | FEEDER |  |  |  |  | CDC | 512 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 西港線 (F11) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.西港線A2 | 11KV西港線 S相AMP | FEEDER |  |  |  |  | CDC | 513 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 西港線 (F11) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.西港線A3 | 11KV西港線 T相AMP | FEEDER |  |  |  |  | CDC | 514 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 西港線 (F11) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.西港線A0 | 11KV西港線 N相AMP | FEEDER |  |  |  |  | CDC | 515 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 佳工線 (F3) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳工線KVAR | 11KV佳工線 KVAR | FEEDER |  |  |  |  | CDC | 516 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 佳工線 (F3) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳工線A1 | 11KV佳工線 R相AMP | FEEDER |  |  |  |  | CDC | 517 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 佳工線 (F3) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳工線A2 | 11KV佳工線 S相AMP | FEEDER |  |  |  |  | CDC | 518 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 佳工線 (F3) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳工線A3 | 11KV佳工線 T相AMP | FEEDER |  |  |  |  | CDC | 519 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 佳工線 (F3) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳工線A0 | 11KV佳工線 N相AMP | FEEDER |  |  |  |  | CDC | 520 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | 佳西線 (F25) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳西線KVAR | 11KV佳西線 KVAR | FEEDER |  |  |  |  | CDC | 521 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 佳西線 (F25) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳西線A1 | 11KV佳西線 R相AMP | FEEDER |  |  |  |  | CDC | 522 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 佳西線 (F25) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳西線A2 | 11KV佳西線 S相AMP | FEEDER |  |  |  |  | CDC | 523 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 佳西線 (F25) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳西線A3 | 11KV佳西線 T相AMP | FEEDER |  |  |  |  | CDC | 524 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 佳西線 (F25) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳西線A0 | 11KV佳西線 N相AMP | FEEDER |  |  |  |  | CDC | 525 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 佳麻線 (F24) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳麻線KVAR | 11KV佳麻線 KVAR | FEEDER |  |  |  |  | CDC | 526 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 佳麻線 (F24) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳麻線A1 | 11KV佳麻線 R相AMP | FEEDER |  |  |  |  | CDC | 527 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 佳麻線 (F24) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳麻線A2 | 11KV佳麻線 S相AMP | FEEDER |  |  |  |  | CDC | 528 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 佳麻線 (F24) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳麻線A3 | 11KV佳麻線 T相AMP | FEEDER |  |  |  |  | CDC | 529 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 佳麻線 (F24) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳麻線A0 | 11KV佳麻線 N相AMP | FEEDER |  |  |  |  | CDC | 530 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 佳塭線 (F17) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳塭線KVAR | 11KV佳塭線 KVAR | FEEDER |  |  |  |  | CDC | 531 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 佳塭線 (F17) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳塭線A1 | 11KV佳塭線 R相AMP | FEEDER |  |  |  |  | CDC | 532 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 佳塭線 (F17) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳塭線A2 | 11KV佳塭線 S相AMP | FEEDER |  |  |  |  | CDC | 533 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 佳塭線 (F17) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳塭線A3 | 11KV佳塭線 T相AMP | FEEDER |  |  |  |  | CDC | 534 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 佳塭線 (F17) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳塭線A0 | 11KV佳塭線 N相AMP | FEEDER |  |  |  |  | CDC | 535 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 佳興線 (F2) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳興線KVAR | 11KV佳興線 KVAR | FEEDER |  |  |  |  | CDC | 536 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 佳興線 (F2) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳興線A1 | 11KV佳興線 R相AMP | FEEDER |  |  |  |  | CDC | 537 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 佳興線 (F2) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳興線A2 | 11KV佳興線 S相AMP | FEEDER |  |  |  |  | CDC | 538 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 佳興線 (F2) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳興線A3 | 11KV佳興線 T相AMP | FEEDER |  |  |  |  | CDC | 539 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 佳興線 (F2) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.佳興線A0 | 11KV佳興線 N相AMP | FEEDER |  |  |  |  | CDC | 540 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 林樂線 (F15) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.林樂線KVAR | 11KV林樂線 KVAR | FEEDER |  |  |  |  | CDC | 541 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 林樂線 (F15) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.林樂線A1 | 11KV林樂線 R相AMP | FEEDER |  |  |  |  | CDC | 542 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 林樂線 (F15) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.林樂線A2 | 11KV林樂線 S相AMP | FEEDER |  |  |  |  | CDC | 543 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 林樂線 (F15) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.林樂線A3 | 11KV林樂線 T相AMP | FEEDER |  |  |  |  | CDC | 544 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 林樂線 (F15) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.林樂線A0 | 11KV林樂線 N相AMP | FEEDER |  |  |  |  | CDC | 545 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 通吉線 (F4) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.通吉線KVAR | 11KV通吉線 KVAR | FEEDER |  |  |  |  | CDC | 546 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 通吉線 (F4) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.通吉線A1 | 11KV通吉線 R相AMP | FEEDER |  |  |  |  | CDC | 547 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 通吉線 (F4) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.通吉線A2 | 11KV通吉線 S相AMP | FEEDER |  |  |  |  | CDC | 548 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 通吉線 (F4) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.通吉線A3 | 11KV通吉線 T相AMP | FEEDER |  |  |  |  | CDC | 549 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 通吉線 (F4) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.通吉線A0 | 11KV通吉線 N相AMP | FEEDER |  |  |  |  | CDC | 550 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 頂城線 (F7) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.頂城線KVAR | 11KV頂城線 KVAR | FEEDER |  |  |  |  | CDC | 551 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 頂城線 (F7) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.頂城線A1 | 11KV頂城線 R相AMP | FEEDER |  |  |  |  | CDC | 552 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 頂城線 (F7) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.頂城線A2 | 11KV頂城線 S相AMP | FEEDER |  |  |  |  | CDC | 553 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 頂城線 (F7) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.頂城線A3 | 11KV頂城線 T相AMP | FEEDER |  |  |  |  | CDC | 554 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 頂城線 (F7) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.頂城線A0 | 11KV頂城線 N相AMP | FEEDER |  |  |  |  | CDC | 555 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 塭寮線 (F9) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.塭寮線KVAR | 11KV塭寮線 KVAR | FEEDER |  |  |  |  | CDC | 556 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 塭寮線 (F9) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.塭寮線A1 | 11KV塭寮線 R相AMP | FEEDER |  |  |  |  | CDC | 557 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 塭寮線 (F9) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.塭寮線A2 | 11KV塭寮線 S相AMP | FEEDER |  |  |  |  | CDC | 558 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 塭寮線 (F9) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.塭寮線A3 | 11KV塭寮線 T相AMP | FEEDER |  |  |  |  | CDC | 559 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 塭寮線 (F9) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.塭寮線A0 | 11KV塭寮線 N相AMP | FEEDER |  |  |  |  | CDC | 560 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 新生線 (F19) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.新生線KVAR | 11KV新生線 KVAR | FEEDER |  |  |  |  | CDC | 561 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 新生線 (F19) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.新生線A1 | 11KV新生線 R相AMP | FEEDER |  |  |  |  | CDC | 562 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 新生線 (F19) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.新生線A2 | 11KV新生線 S相AMP | FEEDER |  |  |  |  | CDC | 563 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 新生線 (F19) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.新生線A3 | 11KV新生線 T相AMP | FEEDER |  |  |  |  | CDC | 564 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 新生線 (F19) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.新生線A0 | 11KV新生線 N相AMP | FEEDER |  |  |  |  | CDC | 565 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 嘉福線 (F13) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.嘉福線KVAR | 11KV嘉福線 KVAR | FEEDER |  |  |  |  | CDC | 566 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 嘉福線 (F13) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.嘉福線A1 | 11KV嘉福線 R相AMP | FEEDER |  |  |  |  | CDC | 567 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 嘉福線 (F13) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.嘉福線A2 | 11KV嘉福線 S相AMP | FEEDER |  |  |  |  | CDC | 568 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 嘉福線 (F13) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.嘉福線A3 | 11KV嘉福線 T相AMP | FEEDER |  |  |  |  | CDC | 569 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 嘉福線 (F13) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.嘉福線A0 | 11KV嘉福線 N相AMP | FEEDER |  |  |  |  | CDC | 570 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 漳洲線 (F6) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漳洲線KVAR | 11KV漳洲線 KVAR | FEEDER |  |  |  |  | CDC | 571 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 漳洲線 (F6) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漳洲線A1 | 11KV漳洲線 R相AMP | FEEDER |  |  |  |  | CDC | 572 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 漳洲線 (F6) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漳洲線A2 | 11KV漳洲線 S相AMP | FEEDER |  |  |  |  | CDC | 573 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 漳洲線 (F6) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漳洲線A3 | 11KV漳洲線 T相AMP | FEEDER |  |  |  |  | CDC | 574 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 漳洲線 (F6) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漳洲線A0 | 11KV漳洲線 N相AMP | FEEDER |  |  |  |  | CDC | 575 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 篤加線 (F14) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.篤加線KVAR | 11KV篤加線 KVAR | FEEDER |  |  |  |  | CDC | 576 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 篤加線 (F14) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.篤加線A1 | 11KV篤加線 R相AMP | FEEDER |  |  |  |  | CDC | 577 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 篤加線 (F14) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.篤加線A2 | 11KV篤加線 S相AMP | FEEDER |  |  |  |  | CDC | 578 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 篤加線 (F14) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.篤加線A3 | 11KV篤加線 T相AMP | FEEDER |  |  |  |  | CDC | 579 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 篤加線 (F14) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.篤加線A0 | 11KV篤加線 N相AMP | FEEDER |  |  |  |  | CDC | 580 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 漚汪線 (F1) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漚汪線KVAR | 11KV漚汪線 KVAR | FEEDER |  |  |  |  | CDC | 581 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 漚汪線 (F1) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漚汪線A1 | 11KV漚汪線 R相AMP | FEEDER |  |  |  |  | CDC | 582 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 漚汪線 (F1) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漚汪線A2 | 11KV漚汪線 S相AMP | FEEDER |  |  |  |  | CDC | 583 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 漚汪線 (F1) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漚汪線A3 | 11KV漚汪線 T相AMP | FEEDER |  |  |  |  | CDC | 584 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 漚汪線 (F1) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.漚汪線A0 | 11KV漚汪線 N相AMP | FEEDER |  |  |  |  | CDC | 585 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC 電壓 |  |  | DCVolt_-50_50(-2000_2000) |  | B3/S76_D1 | [8 empty] | 佳一SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 586 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | KN01 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備01線KVAR | 11KV備01線 KVAR | FEEDER | [5 empty] | 587 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | KN01 R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備01線A1 | 11KV備01線 R相AMP | FEEDER | [5 empty] | 588 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | KN01 S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備01線A2 | 11KV備01線 S相AMP | FEEDER | [5 empty] | 589 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | KN01 T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備01線A3 | 11KV備01線 T相AMP | FEEDER | [5 empty] | 590 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | KN01 N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備01線A0 | 11KV備01線 N相AMP | FEEDER | [5 empty] | 591 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | #2BUS | #2BUS |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0013 |  |  | 1-8D |  |  | 69KV BUS#2 電壓 |  |  | kV_-90_90(-2000_2000) | aab | B2/S76_A1 | [8 empty] | 佳一SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | [5 empty] | 592 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | I |  | INSERT | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 600 R相電流 |  |  | A_-1200_1200(-2000_2000) |  | B2/S76_A1 | [8 empty] | 佳一SS.600TIE_AMP | 600TIE AMP | TIE | [5 empty] | 593 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [5 empty] | C12R1200 | 1140 | 1200 | 1201 | 1202 | 0 | -1140 | -1200 | -1201 | -1202 | 1 | 0.01 | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 2BBUS | #2BBUS |  | V_R |  | INSERT | MvMoment | R相電壓 |  | Y |  | AI |  | BUS |  |  |  |  | 0219 |  |  | 2-DB |  |  | #2B 11KV R相電壓 |  |  | kV_-9_9(-2000_2000) | aba | B2/S76_D1 | [8 empty] | 佳一SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 594 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | KN02 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備02線KVAR | 11KV備02線 KVAR | FEEDER | [5 empty] | 595 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | KN02 R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備02線A1 | 11KV備02線 R相AMP | FEEDER | [5 empty] | 596 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | KN02 S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備02線A2 | 11KV備02線 S相AMP | FEEDER | [5 empty] | 597 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | KN02 T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備02線A3 | 11KV備02線 T相AMP | FEEDER | [5 empty] | 598 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | KN02 N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S76_D1 | [8 empty] | 佳一SS.備02線A0 | 11KV備02線 N相AMP | FEEDER | [5 empty] | 599 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | #1TR 63Q |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | [5 empty] | 600 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | #1TR 96B1 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | [5 empty] | 601 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | #1TR 96B2 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | [5 empty] | 602 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | #1TR 96D |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | [5 empty] | 603 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | #1TR 96P |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | [5 empty] | 604 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #2TR 63Q |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | [5 empty] | 605 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #2TR 96B1 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | [5 empty] | 606 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | #2TR 96B2 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | [5 empty] | 607 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | #2TR 96D |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | [5 empty] | 608 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | #2TR 96P |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | [5 empty] | 609 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | #3TR 63Q |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | [5 empty] | 610 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | #3TR 96B1 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | [5 empty] | 611 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | #3TR 96B2 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | [5 empty] | 612 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | #3TR 96D |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | [5 empty] | 613 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | #3TR 96P |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | [5 empty] | 614 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | #4TR 63Q |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_63Q | #4MTR ULTC電驛動作 | OTHER | [5 empty] | 615 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | #4TR 96B1 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_96B1 | #4MTR 撲氣電驛警報 | OTHER | [5 empty] | 616 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #4TR 96B2 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_96B2 | #4MTR 撲氣電驛動作 | OTHER | [5 empty] | 617 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | #4TR 96D |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_96D | #4MTR 放壓電驛動作 | OTHER | [5 empty] | 618 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | #4TR 96P |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_96P | #4MTR 突壓電驛動作 | OTHER | [5 empty] | 619 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-06 |  |  | #5TR 63Q |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_63Q | #5MTR ULTC電驛動作 | OTHER | [5 empty] | 620 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | #5TR 96B1 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_96B1 | #5MTR 撲氣電驛警報 | OTHER | [5 empty] | 621 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0F-00 |  |  | #5TR 96B2 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_96B2 | #5MTR 撲氣電驛動作 | OTHER | [5 empty] | 622 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #5TR 96D |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_96D | #5MTR 放壓電驛動作 | OTHER | [5 empty] | 623 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | #5TR 96P |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_96P | #5MTR 突壓電驛動作 | OTHER | [5 empty] | 624 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0665 |  |  | 2-13-01 |  |  | KN01 PH RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN01_PHA | 11KV備01線(KN01) 相間RY | FEEDER | [5 empty] | 625 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0666 |  |  | 2-13-02 |  |  | KN01 GD RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN01_GDA | 11KV備01線(KN01) 接地RY | FEEDER | [5 empty] | 626 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | 79UL |  | INSERT | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0149 | 2-30-13 |  | 2-15 | KN01 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN01_79UL | 11KV備01線(KN01) 79RY U/L | FEEDER | [5 empty] | 627 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0857 |  | 0177 | 2-35-09 |  | 2-31 | KN01 LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN01_ADJ | 11KV備01線(KN01) LCO分流器 U/L | FEEDER | [5 empty] | 628 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | L/KN01/T1 |  |  | 0664 |  | 0147 | 2-13-00 |  | 2-13 | KN01 CB |  |  |  | aaib | B2/S76_D1 | [8 empty] | 佳一SS.KN01_CB | KN01(11KV備01線) CB | FEEDER | [5 empty] | 629 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | SSTR1 PH RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 630 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0155 |  |  | 1-13-03 |  |  | SSTR1 GD RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 631 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0864 | 865 | 0032 | 2-36-00 | 2-36-01 | 1-20 | #1TR 1DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.751_DS | 751(#1MTR) DS | DTR | [5 empty] | 632 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0866 | 867 | 0033 | 2-36-02 | 2-36-03 | 1-21 | #1TR 2DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.752_DS | 752(#1MTR) DS | DTR | [5 empty] | 633 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 |  |  | 1-1B-07 |  |  | M-1 81 RY |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.1M_81A | 1M(#1MTR) 81RY | OTHER | [5 empty] | 634 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M1 | #1MTR(M1) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0319 |  | 0067 | 1-33-15 |  | 1-43 | M-1 81RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.1M_81UL | 1M(#1MTR) 81RY U/L | OTHER | [5 empty] | 635 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0667 |  |  | 2-13-03 |  |  | KN01 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN01_81A | KN01 81RY | OTHER | [5 empty] | 636 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0463 |  |  | 1-3C-15 |  |  | KN01 LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN01_LOA | 備01線 復閉失敗閉鎖 | OTHER | [5 empty] | 637 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0654 |  |  | 2-11-06 |  |  | 漚汪線 (F1) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN21_81A | KN21 81RY | OTHER | [5 empty] | 638 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | 漚汪線 (F1) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN21_LOA | 漚汪線 復閉失敗閉鎖 | OTHER | [5 empty] | 639 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0655 |  |  | 2-11-07 |  |  | 佳興線 (F2) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN22_81A | KN22 81RY | OTHER | [5 empty] | 640 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | 佳興線 (F2) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN22_LOA | 佳興線 復閉失敗閉鎖 | OTHER | [5 empty] | 641 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0656 |  |  | 2-12-00 |  |  | 佳工線 (F3) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN23_81A | KN23 81RY | OTHER | [5 empty] | 642 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | 佳工線 (F3) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN23_LOA | 佳工線 復閉失敗閉鎖 | OTHER | [5 empty] | 643 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0657 |  |  | 2-12-01 |  |  | 通吉線 (F4) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN24_81A | KN24 81RY | OTHER | [5 empty] | 644 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | 通吉線 (F4) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN24_LOA | 通吉線 復閉失敗閉鎖 | OTHER | [5 empty] | 645 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0658 |  |  | 2-12-02 |  |  | 佳25線 (F5) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN25_81A | KN25 81RY | OTHER | [5 empty] | 646 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0484 |  |  | 1-3E-04 |  |  | 佳25線 (F5) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN25_LOA | 佳25線 復閉失敗閉鎖 | OTHER | [5 empty] | 647 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2A | B/1BUS | B/2BUS |  |  | 0144 |  | 0007 | 1-12-00 |  | 1-07 | 69KV TIE CB |  |  |  | aagz | B2/S76_A1 | [8 empty] | 佳一SS.600_CB | 600(TIE) CB | TIE | [5 empty] | 648 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0884 | 885 | 0028 | 2-37-04 | 2-37-05 | 1-1C | 69KV TIE 1DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.601_DS | 601(TIE) DS | TIE | [5 empty] | 649 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0886 | 887 | 0029 | 2-37-06 | 2-37-07 | 1-1D | 69KV TIE 2DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.602_DS | 602(TIE) DS | TIE | [5 empty] | 650 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | #2BUS | #2BUS |  | BUS_VUA |  | INSERT | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0286 |  |  | 1-31-14 |  |  | 69KV BUS #2 衡相監視 |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | [5 empty] | 651 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  | INSERT | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | 69KV TIE 1GDA |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.600GDA(1) | 69KV #1BUS TIE(600) 67N | OTHER | [5 empty] | 652 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  | INSERT | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | 69KV TIE 2GDA |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.600GDA(2) | 69KV #2BUS TIE(600) 67N | OTHER | [5 empty] | 653 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  | INSERT | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | 69KV TIE 1PHA |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.600PHA(1) | 69KV #1BUS TIE(600) 67 | OTHER | [5 empty] | 654 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  | INSERT | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | 69KV TIE 2PHA |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.600PHA(2) | 69KV #2BUS TIE(600) 67 | OTHER | [5 empty] | 655 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | 69KV #1BUS 87A |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69KV1BUS_87A | 69KV #1BUS 87B1A | OTHER | [5 empty] | 656 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0296 |  | 0013 | 1-32-08 |  | 1-0D | 69KV #1BUS 87 U/L |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69KV1BUS_87UL | 69KV #1BUS 87RY UL | OTHER | [5 empty] | 657 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | #2BUS | #2BUS |  | 87A |  | INSERT | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | 69KV #2BUS 87A |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69KV2BUS_87A | 69KV #2BUS 87B2A | OTHER | [5 empty] | 658 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | #2BUS | #2BUS |  | 87UL |  | INSERT | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0297 |  | 0014 | 1-32-09 |  | 1-0E | 69KV #2BUS 87 U/L |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69KV2BUS_87UL | 69KV #2BUS 87RY UL | OTHER | [5 empty] | 659 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | ComPoint |  |  | 12B_CTFA | 69KV BUS CT迴路故障 | INSERT | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0299 |  |  | 1-32-11 |  |  | 69KV BUS RY CTFA |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | [5 empty] | 660 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | ComPoint |  |  | BUS_RYFA | 69KV BUS IED故障 | INSERT | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0298 |  |  | 1-32-10 |  |  | 69KV BUS RY RYFA |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.69KV_BUS_RYFA | 69KV BUS IED故障 | OTHER | [5 empty] | 661 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | RYFA | 69KV TIE IED故障 | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | 69KV TIE RYFA |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.69KV_TIE_RYFA | 69KV TIE IED故障 | OTHER | [5 empty] | 662 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0669 |  |  | 2-13-05 |  |  | KN02 PH RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN02_PHA | 11KV備02線(KN02) 相間RY | FEEDER | [5 empty] | 663 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0670 |  |  | 2-13-06 |  |  | KN02 GD RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN02_GDA | 11KV備02線(KN02) 接地RY | FEEDER | [5 empty] | 664 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | 79UL |  | INSERT | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0150 | 2-30-14 |  | 2-16 | KN02 79RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN02_79UL | 11KV備02線(KN02) 79RY U/L | FEEDER | [5 empty] | 665 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | ADJ |  | INSERT | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0858 |  | 0178 | 2-35-10 |  | 2-32 | KN02 LCO ADJ U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN02_ADJ | 11KV備02線(KN02) LCO分流器 U/L | FEEDER | [5 empty] | 666 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | L/KN02/T1 |  |  | 0668 |  | 0148 | 2-13-04 |  | 2-14 | KN02 CB |  |  |  | abcb | B2/S76_D1 | [8 empty] | 佳一SS.KN02_CB | KN02(11KV備02線) CB | FEEDER | [5 empty] | 667 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/1BUS | T/1SSTR |  |  | 0153 |  | 0066 | 1-13-01 |  | 1-42 | SSTR1 CB |  |  |  | aabb | B2/S76_D1 | [8 empty] | 佳一SS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 668 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M2B | #2MTR(M2B) |  | CB |  | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbG | B/2BBUS | T/2MTR |  |  | 0012 |  | 0070 | 1-01-04 |  | 1-46 | #2TR 二次 (B) CB |  |  |  | abeb | B2/S76_D1 | [8 empty] | 佳一SS.2MB_CB | 2MB(#2MTR) CB | DTR | [5 empty] | 669 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 51A |  | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | #2TR 二次 (B) 51 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | [5 empty] | 670 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | #2TR 二次 (B) 51N RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.#2_MB_51NA | #2MB GDA | OTHER | [5 empty] | 671 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | M2A 81RY |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.2MA_81A | 2MA(#2MTR) 81RY | OTHER | [5 empty] | 672 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M2A | #2MTR(M2A) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0087 | 2-31-14 |  | 1-57 | M2A 81RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.2MA_81UL | 2MA(#2MTR) 81RY U/L | OTHER | [5 empty] | 673 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | M2B 81RY |  |  |  |  | ELEM/S76_D1 | [8 empty] | 佳一SS.2MB_81A | 2MB(#2MTR) 81RY | OTHER | [5 empty] | 674 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | M2B | #2MTR(M2B) |  | 81UL |  | INSERT | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  | 0107 | 2-31-15 |  | 1-6B | M2B 81RY U/L |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.2MB_81UL | 2MB(#2MTR) 81RY U/L | OTHER | [5 empty] | 675 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0671 |  |  | 2-13-07 |  |  | KN02 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN02_81A | KN02 81RY | OTHER | [5 empty] | 676 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | KN02 LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN02_LOA | 備02線 復閉失敗閉鎖 | OTHER | [5 empty] | 677 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0659 |  |  | 2-12-03 |  |  | 漳洲線 (F6) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN26_81A | KN26 81RY | OTHER | [5 empty] | 678 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0485 |  |  | 1-3E-05 |  |  | 漳洲線 (F6) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN26_LOA | 漳洲線 復閉失敗閉鎖 | OTHER | [5 empty] | 679 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0660 |  |  | 2-12-04 |  |  | 頂城線 (F7) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN27_81A | KN27 81RY | OTHER | [5 empty] | 680 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0486 |  |  | 1-3E-06 |  |  | 頂城線 (F7) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN27_LOA | 頂城線 復閉失敗閉鎖 | OTHER | [5 empty] | 681 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0661 |  |  | 2-12-05 |  |  | 七股線 (F8) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN28_81A | KN28 81RY | OTHER | [5 empty] | 682 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0487 |  |  | 1-3E-07 |  |  | 七股線 (F8) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN28_LOA | 七股線 復閉失敗閉鎖 | OTHER | [5 empty] | 683 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0662 |  |  | 2-12-06 |  |  | 塭寮線 (F9) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN29_81A | KN29 81RY | OTHER | [5 empty] | 684 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | 塭寮線 (F9) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN29_LOA | 塭寮線 復閉失敗閉鎖 | OTHER | [5 empty] | 685 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0663 |  |  | 2-12-07 |  |  | 佳30線 (F10) 81 RY |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN30_81A | KN30 81RY | OTHER | [5 empty] | 686 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0489 |  |  | 1-3E-09 |  |  | 佳30線 (F10) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN30_LOA | 佳30線 復閉失敗閉鎖 | OTHER | [5 empty] | 687 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0888 | 889 | 0030 | 2-37-08 | 2-37-09 | 1-1E | 69KV SC 1DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.811_DS | 811(69KV #1SC) DS | SC | [5 empty] | 688 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0890 | 891 | 0031 | 2-37-10 | 2-37-11 | 1-1F | 69KV SC 2DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.812_DS | 812(69KV #1SC) DS | SC | [5 empty] | 689 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | DS1 | 621 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0180 | 2-38-00 | 2-38-01 | 2-34 | #620學甲佳里二路 1DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.621_DS | 621(學甲佳里二路) DS | LINE69 | [5 empty] | 690 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | DS2 | 622 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0181 | 2-38-02 | 2-38-03 | 2-35 | #620學甲佳里二路 2DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.622_DS | 622(學甲佳里二路) DS | LINE69 | [5 empty] | 691 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | DS3 | 623 | INSERT | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0182 | 2-38-04 | 2-38-05 | 2-36 | #620學甲佳里二路 3DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.623_DS | 623(學甲佳里二路) DS | LINE69 | [5 empty] | 692 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | ES3 | 623E | INSERT | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 | 903 | 0183 | 2-38-06 | 2-38-07 | 2-37 | #620學甲佳里二路 3EDS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.623E_ES | 623E(學甲佳里二路) ES | LINE69 | [5 empty] | 693 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | 西港線 (F11) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN31_LOA | 西港線 復閉失敗閉鎖 | OTHER | [5 empty] | 694 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | 子良線 (F12) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN32_LOA | 子良線 復閉失敗閉鎖 | OTHER | [5 empty] | 695 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | 嘉福線 (F13) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN33_LOA | 嘉福線 復閉失敗閉鎖 | OTHER | [5 empty] | 696 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | 篤加線 (F14) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN34_LOA | 篤加線 復閉失敗閉鎖 | OTHER | [5 empty] | 697 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | 林樂線 (F15) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN35_LOA | 林樂線 復閉失敗閉鎖 | OTHER | [5 empty] | 698 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0502 |  |  | 1-3F-06 |  |  | 三股線 (F16) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN36_LOA | 三股線 復閉失敗閉鎖 | OTHER | [5 empty] | 699 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0503 |  |  | 1-3F-07 |  |  | 佳塭線 (F17) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN37_LOA | 佳塭線 復閉失敗閉鎖 | OTHER | [5 empty] | 700 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0504 |  |  | 1-3F-08 |  |  | 光復線 (F18) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN38_LOA | 光復線 復閉失敗閉鎖 | OTHER | [5 empty] | 701 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0505 |  |  | 1-3F-09 |  |  | 新生線 (F19) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN39_LOA | 新生線 復閉失敗閉鎖 | OTHER | [5 empty] | 702 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0506 |  |  | 1-3F-10 |  |  | 仁愛線 (F20) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN40_LOA | 仁愛線 復閉失敗閉鎖 | OTHER | [5 empty] | 703 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0508 |  |  | 1-3F-12 |  |  | 北農線 (F22) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN41_LOA | 北農線 復閉失敗閉鎖 | OTHER | [5 empty] | 704 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0509 |  |  | 1-3F-13 |  |  | 中山線 (F23) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN42_LOA | 中山線 復閉失敗閉鎖 | OTHER | [5 empty] | 705 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0510 |  |  | 1-3F-14 |  |  | 佳麻線 (F24) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN43_LOA | 佳麻線 復閉失敗閉鎖 | OTHER | [5 empty] | 706 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0511 |  |  | 1-3F-15 |  |  | 佳西線 (F25) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN44_LOA | 佳西線 復閉失敗閉鎖 | OTHER | [5 empty] | 707 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0507 |  |  | 1-3F-11 |  |  | 佳45線 (F21) LOA |  |  |  |  | B2/S76_D1 | [8 empty] | 佳一SS.KN45_LOA | 佳45線 復閉失敗閉鎖 | OTHER | [5 empty] | 708 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | DS1 | 731 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0188 | 2-39-00 | 2-39-01 | 2-3C | #730學甲佳里一路 1DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.731_DS | 731(學甲佳里一路) DS | LINE69 | [5 empty] | 709 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | DS2 | 732 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0189 | 2-39-02 | 2-39-03 | 2-3D | #730學甲佳里一路 2DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.732_DS | 732(學甲佳里一路) DS | LINE69 | [5 empty] | 710 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | DS3 | 733 | INSERT | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0190 | 2-39-04 | 2-39-05 | 2-3E | #730學甲佳里一路 3DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.733_DS | 733(學甲佳里一路) DS | LINE69 | [5 empty] | 711 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | ES3 | 733E | INSERT | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 | 919 | 0191 | 2-39-06 | 2-39-07 | 2-3F | #730學甲佳里一路 3EDS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.733E_ES | 733E(學甲佳里一路) ES | LINE69 | [5 empty] | 712 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | DS1 | 781 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0876 | 877 | 0038 | 2-36-12 | 2-36-13 | 1-26 | #4TR 1DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.781_DS | 781(#4MTR) DS | DTR | [5 empty] | 713 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0868 | 869 | 0034 | 2-36-04 | 2-36-05 | 1-22 | #2TR 1DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.761_DS | 761(#2MTR) DS | DTR | [5 empty] | 714 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0870 | 871 | 0035 | 2-36-06 | 2-36-07 | 1-23 | #2TR 2DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.762_DS | 762(#2MTR) DS | DTR | [5 empty] | 715 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | DS1 | 651 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0184 | 2-38-08 | 2-38-09 | 2-38 | #650麻豆佳里線 1DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.651_DS | 651(佳里麻豆線) DS | LINE69 | [5 empty] | 716 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | DS2 | 652 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 907 | 0185 | 2-38-10 | 2-38-11 | 2-39 | #650麻豆佳里線 2DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.652_DS | 652(佳里麻豆線) DS | LINE69 | [5 empty] | 717 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | DS3 | 653 | INSERT | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0186 | 2-38-12 | 2-38-13 | 2-3A | #650麻豆佳里線 3DS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.653_DS | 653(佳里麻豆線) DS | LINE69 | [5 empty] | 718 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | ES3 | 653E | INSERT | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0910 | 911 | 0187 | 2-38-14 | 2-38-15 | 2-3B | #650麻豆佳里線 3EDS-AS |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.653E_ES | 653E(佳里麻豆線) ES | LINE69 | [5 empty] | 719 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0872 | 873 | 0036 | 2-36-08 | 2-36-09 | 1-24 | #3TR 1DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.771_DS | 771(#3MTR) DS | DTR | [5 empty] | 720 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0874 | 875 | 0037 | 2-36-10 | 2-36-11 | 1-25 | #3TR 2DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.772_DS | 772(#3MTR) DS | DTR | [5 empty] | 721 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 漚汪線 (F1) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 722 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | 佳興線 (F2) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 723 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 佳工線 (F3) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 724 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | 通吉線 (F4) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 725 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | 漳洲線 (F6) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 726 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 頂城線 (F7) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 727 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | 七股線 (F8) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 728 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | 塭寮線 (F9) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 729 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0010 |  |  | 1-4A |  |  | 西港線 (F11) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 730 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0011 |  |  | 1-4B |  |  | 子良線 (F12) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 731 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0012 |  |  | 1-4C |  |  | 嘉福線 (F13) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 732 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0013 |  |  | 1-4D |  |  | 篤加線 (F14) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 733 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0014 |  |  | 1-4E |  |  | 林樂線 (F15) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 734 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | 三股線 (F16) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 735 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0016 |  |  | 1-50 |  |  | 佳塭線 (F17) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 736 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0017 |  |  | 1-51 |  |  | 光復線 (F18) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 737 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | 新生線 (F19) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 738 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0019 |  |  | 1-53 |  |  | 仁愛線 (F20) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 739 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0021 |  |  | 1-55 |  |  | 北農線 (F22) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 740 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0022 |  |  | 1-56 |  |  | 中山線 (F23) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 741 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0023 |  |  | 1-57 |  |  | 佳麻線 (F24) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 742 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0024 |  |  | 1-58 |  |  | 佳西線 (F25) KWH(+) |  |  |  |  | B2/S76_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 743 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN01_DS | KN01_DS (非取樣點) | FEEDER | [5 empty] | 744 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | ES | KN01_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN01_ES | KN01_ES (非取樣點) | FEEDER | [5 empty] | 745 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN21_DS | KN21_DS (非取樣點) | FEEDER | [5 empty] | 746 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN22_DS | KN22_DS (非取樣點) | FEEDER | [5 empty] | 747 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN23_DS | KN23_DS (非取樣點) | FEEDER | [5 empty] | 748 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN24_DS | KN24_DS (非取樣點) | FEEDER | [5 empty] | 749 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN25_DS | KN25_DS (非取樣點) | FEEDER | [5 empty] | 750 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | ES | KN25_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN25_ES | KN25_ES (非取樣點) | FEEDER | [5 empty] | 751 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 1BR | #1BR |  | DS | 1BR_DS (非取樣點) | DELETE | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.1BR_DS | 1BR_DS (非取樣點) | TIE | [5 empty] | 752 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 1BR | #1BR |  | ES | 1BR_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.1BR_ES | 1BR ES(非取樣點) | OTHER | [5 empty] | 753 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.601E | 601E (非取樣點) | TIE | [5 empty] | 754 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.602E | 602E (非取樣點) | TIE | [5 empty] | 755 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.750TE | 750TE (非取樣點) | DTR | [5 empty] | 756 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.750BE | 750BE (非取樣點) | DTR | [5 empty] | 757 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | #2BUS | #2BUS |  | BE2 | 69B2E (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 758 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN02_DS | KN02_DS (非取樣點) | FEEDER | [5 empty] | 759 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | ES | KN02_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN02_ES | KN02_ES (非取樣點) | FEEDER | [5 empty] | 760 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN26_DS | KN26_DS (非取樣點) | FEEDER | [5 empty] | 761 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN27_DS | KN27_DS (非取樣點) | FEEDER | [5 empty] | 762 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN28_DS | KN28_DS (非取樣點) | FEEDER | [5 empty] | 763 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN29_DS | KN29_DS (非取樣點) | FEEDER | [5 empty] | 764 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | DS1 | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.KN30_DS | KN30_DS (非取樣點) | FEEDER | [5 empty] | 765 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | #2BR | #2BR |  | DS | (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP |  | BayFdrC | B/2ABUS | [13 empty] | accb | B2/S76_D1 | [8 empty] | 佳一SS.2BR_DS | 2BR_DS (非取樣點) | TIE | [5 empty] | 766 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 390 | #1SSTR(390) |  | DS1 | 391 (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.391 | 391 (非取樣點) | OTHER | [5 empty] | 767 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 390 | #1SSTR(390) |  | ES | 391E (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.391E | 391E (非取樣點) | OTHER | [5 empty] | 768 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | M2B | #2MTR(M2B) |  | DS1 | 2MB_ (非取樣點) | INSERT | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.2MB_DS | 2MB_DS (非取樣點) | DTR | [5 empty] | 769 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | M2B | #2MTR(M2B) |  | ES | 2MB_ES (非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.2MB_ES | 2MB_ES (非取樣點) | DTR | [5 empty] | 770 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | #2BR | #2BR |  | DS | 2BR DS(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.2BR_ES | 2BR ES(非取樣點) | OTHER | [5 empty] | 771 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | E1 | #2MB-#1(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.TIE1_ES | #2B-#1 TIE ES(非取樣點) | OTHER | [5 empty] | 772 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | 810BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.810BE | 810BE (非取樣點) | SC | [5 empty] | 773 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | BE0 | 620BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 774 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | BE0 | 730BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.730BE | 730BE (非取樣點) | LINE69 | [5 empty] | 775 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 1BUS | #1BUS |  | BE0 | #1 BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.#1_BE | #1 BE(非取樣點) | OTHER | [5 empty] | 776 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 2ABUS | #2ABUS |  | BE0 | #2A BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 777 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | 2BBUS | #2BBUS |  | BE0 | #2B BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 778 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | TE0 | 790TE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.790TE | 790TE (非取樣點) | DTR | [5 empty] | 779 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | BE0 | 790BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.790BE | 790BE (非取樣點) | DTR | [5 empty] | 780 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.780TE | 780TE (非取樣點) | DTR | [5 empty] | 781 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.780BE | 780BE (非取樣點) | DTR | [5 empty] | 782 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.760TE | 760TE (非取樣點) | DTR | [5 empty] | 783 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.760BE | 760BE (非取樣點) | DTR | [5 empty] | 784 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | BE0 | 650BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.650BE | 650BE (非取樣點) | LINE69 | [5 empty] | 785 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.770TE | 770TE (非取樣點) | DTR | [5 empty] | 786 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S76_D1 | [8 empty] | 佳一SS.770BE | 770BE (非取樣點) | DTR | [5 empty] | 787 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | DS1 | 791 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0880 | 881 | 0040 | 2-37-00 | 2-37-01 | 1-28 | #5TR 1DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.791_DS | 791(#5MTR) DS | DTR | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | DS2 | 792 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0882 | 883 | 0041 | 2-37-02 | 2-37-03 | 1-29 | #5TR 2DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.792_DS | 792(#5MTR) DS | DTR | [5 empty] | 789 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | DS2 | 782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0878 | 879 | 0039 | 2-36-14 | 2-36-15 | 1-27 | #4TR 2DS-AS |  |  |  |  | B3/S76_D1 | [8 empty] | 佳一SS.782_DS | 782(#4MTR) DS | DTR | [5 empty] | 790 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0449 |  |  | 1-3C-01 |  |  | #1DTR 51ZLS |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_51ZUL | #1MTR 51Z U/L | OTHER | [5 empty] | 791 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | #1DTR 86A |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_86A | #1MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 792 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0448 |  |  | 1-3C-00 |  |  | #1DTR 87LS2S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#1MTR_87UL2 | #1MTR 第二套87RY U/L | OTHER | [5 empty] | 793 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0451 |  |  | 1-3C-03 |  |  | #2DTR 51ZLS |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_51ZUL | #2MTR 51Z U/L | OTHER | [5 empty] | 794 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | #2DTR 86A |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_86A | #2MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 795 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0450 |  |  | 1-3C-02 |  |  | #2DTR 87LS2S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#2MTR_87UL2 | #2MTR 第二套87RY U/L | OTHER | [5 empty] | 796 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0453 |  |  | 1-3C-05 |  |  | #3DTR 51ZLS |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_51ZUL | #3MTR 51Z U/L | OTHER | [5 empty] | 797 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | #3DTR 86A |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_86A | #3MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 798 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0452 |  |  | 1-3C-04 |  |  | #3DTR 87LS2S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#3MTR_87UL2 | #3MTR 第二套87RY U/L | OTHER | [5 empty] | 799 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0455 |  |  | 1-3C-07 |  |  | #4DTR 51ZLS |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_51ZUL | #4MTR 51Z U/L | OTHER | [5 empty] | 800 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | #4DTR 86A |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_86A | #4MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 801 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0454 |  |  | 1-3C-06 |  |  | #4DTR 87LS2S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#4MTR_87UL2 | #4MTR 第二套87RY U/L | OTHER | [5 empty] | 802 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 5MTR | #4MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0457 |  |  | 1-3C-09 |  |  | #5DTR 51ZLS |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_51ZUL | #5MTR 51Z U/L | OTHER | [5 empty] | 803 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 5MTR | #4MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | #5DTR 86A |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_86A | #5MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 804 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS |  |  | 5MTR | #4MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0456 |  |  | 1-3C-08 |  |  | #5DTR 87LS2S |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.#5MTR_87UL2 | #5MTR 第二套87RY U/L | OTHER | [5 empty] | 805 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 0 |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0458 |  |  | 1-3C-10 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S76_D1 | [8 empty] | 佳一SS.MTR_IED故障 | MTR IED故障 | OTHER | [5 empty] | 806 | GENERICDIPoint | SS404_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | 1AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值1 |  | Y |  | AI | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 807 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | 2AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值2 |  | Y |  | AI | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 808 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | 3AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值3 |  | Y |  | AI | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 809 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | 4AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值4 |  | Y |  | AI | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 810 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | 5AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值5 |  | Y |  | AI | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.260_SC_CAP | 11KV#5SC 容量 | SC | [5 empty] | 811 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0292 |  | 0010 | 1-32-04 |  | 1-0A | #730學甲佳里一路 87RY U/L |  |  |  |  | B2/S76_A1 | [8 empty] | 佳一SS.730_87UL | 730學甲佳里一路87RY UL | OTHER |  |  |  |  | CDC | 812 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | CE0 | 810CE(非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_A1 | [8 empty] | 佳一SS.810CE | 810CE (非取樣點) | SC | [5 empty] | 813 | [5 empty] | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE1 | TIE(TIE1) |  | D2 | #2MB-#1(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S76_D1 | [8 empty] | 佳一SS.TIE1_DS | #2B-#1 TIE_DS (非取樣點) | TIE | [5 empty] | 243 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/S76_D1 | [12 empty] | 佳一SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: S76/69/1BUS/V; OPRD2: S76/69/2BUS/V
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/S76_D1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: S76/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S76_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_8 | OPRD1: S76/11/M1/MW; OPRD2: S76/11/M2A/MW; OPRD3: S76/11/M3/MW; OPRD4: S76/11/M4/MW; OPRD5: S76/11/M5/MW; OPRD6: S76/69/620/MW; OPRD7: S76/69/650/MW; OPRD8: S76/69/730/MW
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S76_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S76/0/CalcPoint/OPRN2_MW
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S76_D1 | [17 empty] | none
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S76_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: S76/0/CalcPoint/OPRN1; OPRD2: S76/0/CalcPoint/OPRN2; OPRD3: S76/0/CalcPoint/PRFL_UL
S76 | 佳里一SS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S76_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S76/11/M1/MW; OPRD2: S76/11/M1/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S76_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S76/11/M2A/MW; OPRD2: S76/11/M2A/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S76_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S76/11/M3/MW; OPRD2: S76/11/M3/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS |  |  | 4MTR | 4MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S76_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S76/11/M4/MW; OPRD2: S76/11/M4/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS |  |  | 5MTR | 5MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S76_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S76/11/M5/MW; OPRD2: S76/11/M5/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲～佳里二路(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S76_A1 | [12 empty] | 佳一SS.620_AMP | 學甲佳里二路 AMP | LINE69 | AMP_CAL | C12R0960 | amp_cal | OPRD1: S76/69/620/MW; OPRD2: S76/69/620/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS | 69 | 69kV | 650 | 麻豆～佳里線(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S76_A1 | [12 empty] | 佳一SS.650_AMP | 佳里麻豆線 AMP | LINE69 | AMP_CAL | C12R0960 | amp_cal | OPRD1: S76/69/650/MW; OPRD2: S76/69/650/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲～佳里一路(730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/S76_A1 | [12 empty] | 佳一SS.730_AMP | 學甲佳里一路 AMP | LINE69 | AMP_CAL | C12R0831 | amp_cal | OPRD1: S76/69/730/MW; OPRD2: S76/69/730/MVAR; OPRD3: S76/0/CalcPoint/Vbs2
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S76_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 佳一SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S76/11/M1/MW; OPRD2: S76/11/M1/MVAR
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S76_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 佳一SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S76/11/M2A/MW; OPRD2: S76/11/M2A/MVAR
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S76_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 佳一SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S76/11/M3/MW; OPRD2: S76/11/M3/MVAR
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S76_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 佳一SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S76/11/M4/MW; OPRD2: S76/11/M4/MVAR
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S76_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 佳一SS.#5MTR_MVA | #5MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S76/11/M5/MW; OPRD2: S76/11/M5/MVAR
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/S76_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S76//1MTR/MVA; OPRD2: 0
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/S76_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S76//2MTR/MVA; OPRD2: 0
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/S76_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S76//3MTR/MVA; OPRD2: 0
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | LOAD | [9 empty] | B1/S76_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S76//4MTR/MVA; OPRD2: 0
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | LOAD | [9 empty] | B1/S76_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S76//5MTR/MVA; OPRD2: 0
S76 | 佳里一SS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/S76_D1 | [12 empty] | 佳一SS.#1MTR_PF | #1MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S76/11/M1/MW; OPRD2: S76/11/M1/MVAR
S76 | 佳里一SS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/S76_D1 | [12 empty] | 佳一SS.#2MTR_PF | #2MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S76/11/M2A/MW; OPRD2: S76/11/M2A/MVAR
S76 | 佳里一SS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/S76_D1 | [12 empty] | 佳一SS.#3MTR_PF | #3MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S76/11/M3/MW; OPRD2: S76/11/M3/MVAR
S76 | 佳里一SS |  |  | 4MTR | #4MTR |  | PF | [9 empty] | B1/S76_D1 | [12 empty] | 佳一SS.#4MTR_PF | #4MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S76/11/M4/MW; OPRD2: S76/11/M4/MVAR
S76 | 佳里一SS |  |  | 5MTR | #5MTR |  | PF | [9 empty] | B1/S76_D1 | [12 empty] | 佳一SS.#5MTR_PF | #5MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S76/11/M5/MW; OPRD2: S76/11/M5/MVAR
S76 | 佳里一SS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/S76_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S76//1MTR/SupLocal; OPRD2: S76//1MTR/Tap Chan; OPRD3: NULL
S76 | 佳里一SS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/S76_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S76//2MTR/SupLocal; OPRD2: S76//2MTR/Tap Chan; OPRD3: NULL
S76 | 佳里一SS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/S76_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S76//3MTR/SupLocal; OPRD2: S76//3MTR/Tap Chan; OPRD3: NULL
S76 | 佳里一SS |  |  | 4MTR | 4MTR |  | TR_PERM | [9 empty] | B1/S76_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S76//4MTR/SupLocal; OPRD2: S76//4MTR/Tap Chan; OPRD3: NULL
S76 | 佳里一SS |  |  | 5MTR | 5MTR |  | TR_PERM | [9 empty] | B1/S76_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S76//5MTR/SupLocal; OPRD2: S76//5MTR/Tap Chan; OPRD3: NULL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN01/I_R; OPRD3: S76/11/KN01/I_S; OPRD4: S76/11/KN01/I_T
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN02/I_R; OPRD3: S76/11/KN02/I_S; OPRD4: S76/11/KN02/I_T
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN21/I_R; OPRD3: S76/11/KN21/I_S; OPRD4: S76/11/KN21/I_T
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN22/I_R; OPRD3: S76/11/KN22/I_S; OPRD4: S76/11/KN22/I_T
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN23/I_R; OPRD3: S76/11/KN23/I_S; OPRD4: S76/11/KN23/I_T
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN24/I_R; OPRD3: S76/11/KN24/I_S; OPRD4: S76/11/KN24/I_T
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN25/I_R; OPRD3: S76/11/KN25/I_S; OPRD4: S76/11/KN25/I_T
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN26/I_R; OPRD3: S76/11/KN26/I_S; OPRD4: S76/11/KN26/I_T
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN27/I_R; OPRD3: S76/11/KN27/I_S; OPRD4: S76/11/KN27/I_T
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN28/I_R; OPRD3: S76/11/KN28/I_S; OPRD4: S76/11/KN28/I_T
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN29/I_R; OPRD3: S76/11/KN29/I_S; OPRD4: S76/11/KN29/I_T
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN30/I_R; OPRD3: S76/11/KN30/I_S; OPRD4: S76/11/KN30/I_T
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN31/I_R; OPRD3: S76/11/KN31/I_S; OPRD4: S76/11/KN31/I_T
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN32/I_R; OPRD3: S76/11/KN32/I_S; OPRD4: S76/11/KN32/I_T
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN33/I_R; OPRD3: S76/11/KN33/I_S; OPRD4: S76/11/KN33/I_T
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN34/I_R; OPRD3: S76/11/KN34/I_S; OPRD4: S76/11/KN34/I_T
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN35/I_R; OPRD3: S76/11/KN35/I_S; OPRD4: S76/11/KN35/I_T
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN36/I_R; OPRD3: S76/11/KN36/I_S; OPRD4: S76/11/KN36/I_T
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN37/I_R; OPRD3: S76/11/KN37/I_S; OPRD4: S76/11/KN37/I_T
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN38/I_R; OPRD3: S76/11/KN38/I_S; OPRD4: S76/11/KN38/I_T
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN39/I_R; OPRD3: S76/11/KN39/I_S; OPRD4: S76/11/KN39/I_T
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN40/I_R; OPRD3: S76/11/KN40/I_S; OPRD4: S76/11/KN40/I_T
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN41/I_R; OPRD3: S76/11/KN41/I_S; OPRD4: S76/11/KN41/I_T
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN42/I_R; OPRD3: S76/11/KN42/I_S; OPRD4: S76/11/KN42/I_T
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN43/I_R; OPRD3: S76/11/KN43/I_S; OPRD4: S76/11/KN43/I_T
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN44/I_R; OPRD3: S76/11/KN44/I_S; OPRD4: S76/11/KN44/I_T
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: S76/11/KN45/I_R; OPRD3: S76/11/KN45/I_S; OPRD4: S76/11/KN45/I_T
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN01/kVA; OPRD2: S76/11/KN01/KVAR
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN02/kVA; OPRD2: S76/11/KN02/KVAR
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN21/kVA; OPRD2: S76/11/KN21/KVAR
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN22/kVA; OPRD2: S76/11/KN22/KVAR
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN23/kVA; OPRD2: S76/11/KN23/KVAR
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN24/kVA; OPRD2: S76/11/KN24/KVAR
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN25/kVA; OPRD2: S76/11/KN25/KVAR
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN26/kVA; OPRD2: S76/11/KN26/KVAR
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN27/kVA; OPRD2: S76/11/KN27/KVAR
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN28/kVA; OPRD2: S76/11/KN28/KVAR
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN29/kVA; OPRD2: S76/11/KN29/KVAR
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN30/kVA; OPRD2: S76/11/KN30/KVAR
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN31/kVA; OPRD2: S76/11/KN31/KVAR
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN32/kVA; OPRD2: S76/11/KN32/KVAR
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN33/kVA; OPRD2: S76/11/KN33/KVAR
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN34/kVA; OPRD2: S76/11/KN34/KVAR
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN35/kVA; OPRD2: S76/11/KN35/KVAR
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN36/kVA; OPRD2: S76/11/KN36/KVAR
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN37/kVA; OPRD2: S76/11/KN37/KVAR
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN38/kVA; OPRD2: S76/11/KN38/KVAR
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN39/kVA; OPRD2: S76/11/KN39/KVAR
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN40/kVA; OPRD2: S76/11/KN40/KVAR
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN41/kVA; OPRD2: S76/11/KN41/KVAR
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN42/kVA; OPRD2: S76/11/KN42/KVAR
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN43/kVA; OPRD2: S76/11/KN43/KVAR
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN44/kVA; OPRD2: S76/11/KN44/KVAR
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S76_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S76/11/KN45/kVA; OPRD2: S76/11/KN45/KVAR
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S76_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_5 | OPRD1: S76/11/M1/MW; OPRD2: S76/11/M2A/MW; OPRD3: S76/11/M3/MW; OPRD4: S76/11/M4/MW; OPRD5: S76/11/M5/MW
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S76_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_5 | OPRD1: S76/11/M1/MVAR; OPRD2: S76/11/M2A/MVAR; OPRD3: S76/11/M3/MVAR; OPRD4: S76/11/M4/MVAR; OPRD5: S76/11/M5/MVAR
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S76_D1 | [12 empty] | 佳一SS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S76/11/210/CB; OPRD2: 6.9; OPRD3: 0
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S76_D1 | [12 empty] | 佳一SS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S76/11/220/CB; OPRD2: 6.9; OPRD3: 0
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S76_D1 | [12 empty] | 佳一SS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S76/11/230/CB; OPRD2: 6.9; OPRD3: 0
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S76_D1 | [12 empty] | 佳一SS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S76/11/240/CB; OPRD2: 6.9; OPRD3: 0
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S76_D1 | [12 empty] | 佳一SS.250_SC_MVAR | 11KV#5SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S76/11/250/CB; OPRD2: 6.9; OPRD3: 0
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S76_A1 | [12 empty] | 佳一SS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: S76/69/810/CB; OPRD2: 69; OPRD3: 0
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S76_D1 | [12 empty] | 佳一SS.變電所重故障 | 佳里變電所重故障點燈 (AD) | OTHER | STATION_FAULT_20 |  | com_alarm_42 | S76//1MTR/63Q | S76//1MTR/96PA | S76//1MTR/TRA | S76//1MTR/96D | S76//1MTR/96B2 | S76//1MTR/96B1 | S76//1MTR/87A | S76//1MTR/51ZA | S76//2MTR/51ZA | S76//2MTR/87A | S76//2MTR/96PA | S76//2MTR/63Q | S76//2MTR/96D | S76//2MTR/96B2 | S76//2MTR/96B1 | S76//2MTR/TRA | S76//3MTR/63Q | S76//3MTR/87A | S76//3MTR/96D | S76//3MTR/96B2 | S76//3MTR/96B1 | S76//3MTR/TRA | S76//3MTR/96PA | S76//3MTR/51ZA | S76//4MTR/63Q | S76//4MTR/87A | S76//4MTR/96B1 | S76//4MTR/96D | S76//4MTR/96B2 | S76//4MTR/51ZA | S76//4MTR/TRA | S76//4MTR/96PA | S76//5MTR/96B1 | S76//5MTR/63Q | S76//5MTR/96D | S76//5MTR/96B2 | S76//5MTR/87A | S76//5MTR/51ZA | S76//5MTR/TRA | S76//5MTR/96PA | S76/69/1BUS/87A | S76/69/2BUS/87A
S76 | 佳里一SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S76_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_5 | OPRD1: S76//1MTR/TRF; OPRD2: S76//2MTR/TRF; OPRD3: S76//3MTR/TRF; OPRD4: S76//4MTR/TRF; OPRD5: S76//5MTR/TRF
S76 | 佳里一SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/0/RTU/RTU_R_L
S76 | 佳里一SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/0/StaDev/PSF
S76 | 佳里一SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/0/StaDev/DCE
S76 | 佳里一SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S76_D1 | [17 empty] | lamp2CC | OPRD1: S76/69/ComPoint/CBA
S76 | 佳里一SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S76_D1 | [17 empty] | lamp2CC | OPRD1: S76/69/ComPoint/CBF
S76 | 佳里一SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S76_D1 | [17 empty] | lamp2CC | OPRD1: S76/69/ComPoint/ABS_89A
S76 | 佳里一SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/0/StaDev/DCA
S76 | 佳里一SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire | 火災警報 |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/0/StaDev/Fire
S76 | 佳里一SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM_CFA |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/0/StaDev/PMA
S76 | 佳里一SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S76_D1 | [17 empty] | lamp2CC | OPRD1: S76/69/ComPoint/CFA
S76 | 佳里一SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S76_D1 | [17 empty] | lamp2CC | OPRD1: S76/69/ComPoint/IRFA
S76 | 佳里一SS | 11 | 11kV | M1_A1 | #1MTR(M1) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/11/M1/81A
S76 | 佳里一SS | 69 | 69kV | ComPoint_D1 |  |  | 12B_CTFA | 69KV BUS CT迴路故障 |  | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S76_D1 | [17 empty] | lamp2CC | OPRD1: S76/69/ComPoint/12B_CTFA
S76 | 佳里一SS | 69 | 69kV | ComPoint_D1 |  |  | BUS_RYFA | 69KV BUS IED故障 |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S76_D1 | [17 empty] | lamp2CC | OPRD1: S76/69/ComPoint/BUS_RYFA
S76 | 佳里一SS | 11 | 11kV | M2A_A1 | #2MTR(M2A) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/11/M2A/81A
S76 | 佳里一SS | 11 | 11kV | M2B_A1 | #2MTR(M2B) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/S76_A1 | [17 empty] | lamp2CC | OPRD1: S76/11/M2B/81A

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S76 | 佳里一SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | S76/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 佳一SS.620_AMP | 學甲佳里二路 AMP | LINE69 | S76/69/620/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C12R0960 | 864.000000 | 864.000000 | 960.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S76 | 佳里一SS | 0 |  |  |  |  | 七股線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.七股線KVA | 11KV七股線KVA | FEEDER |  |  | KVA_CAL |  |  | 4 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 七股線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.七股線KW | 11KV七股線KW | FEEDER |  |  | KW_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 三股線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.三股線KVA | 11KV三股線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 三股線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.三股線KW | 11KV三股線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 子良線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.子良線KVA | 11KV子良線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 子良線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.子良線KW | 11KV子良線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 中山線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.中山線KVA | 11KV中山線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 中山線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.中山線KW | 11KV中山線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 仁愛線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.仁愛線KVA | 11KV仁愛線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 仁愛線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.仁愛線KW | 11KV仁愛線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 北農線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.北農線KVA | 11KV北農線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 北農線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.北農線KW | 11KV北農線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 光復線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.光復線KVA | 11KV光復線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 光復線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.光復線KW | 11KV光復線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 西港線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.西港線KVA | 11KV西港線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 西港線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.西港線KW | 11KV西港線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳工線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳工線KVA | 11KV佳工線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳工線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳工線KW | 11KV佳工線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳西線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳西線KVA | 11KV佳西線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳西線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳西線KW | 11KV佳西線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳麻線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳麻線KVA | 11KV佳麻線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳麻線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳麻線KW | 11KV佳麻線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳塭線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳塭線KVA | 11KV佳塭線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳塭線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳塭線KW | 11KV佳塭線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳興線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳興線KVA | 11KV佳興線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳興線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳興線KW | 11KV佳興線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 林樂線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.林樂線KVA | 11KV林樂線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 林樂線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.林樂線KW | 11KV林樂線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 通吉線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.通吉線KVA | 11KV通吉線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 通吉線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.通吉線KW | 11KV通吉線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 頂城線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.頂城線KVA | 11KV頂城線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 頂城線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.頂城線KW | 11KV頂城線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 塭寮線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.塭寮線KVA | 11KV塭寮線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 塭寮線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.塭寮線KW | 11KV塭寮線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 新生線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.新生線KVA | 11KV新生線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 新生線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.新生線KW | 11KV新生線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 嘉福線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.嘉福線KVA | 11KV嘉福線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 嘉福線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.嘉福線KW | 11KV嘉福線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 漳洲線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.漳洲線KVA | 11KV漳洲線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 漳洲線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.漳洲線KW | 11KV漳洲線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 篤加線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.篤加線KVA | 11KV篤加線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 篤加線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.篤加線KW | 11KV篤加線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 漚汪線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.漚汪線KVA | 11KV漚汪線KVA | FEEDER |  |  | KVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 漚汪線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.漚汪線KW | 11KV漚汪線KW | FEEDER |  |  | KW_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_MVA | #1MTR二次側 MVA | DTR | S76//1MTR/MVA |  | MVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_PF | #1MTR 功率因素 | DTR | S76//1MTR/PF |  | RPDC_PF_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_MVA | #2MTR二次側 MVA | DTR | S76//2MTR/MVA |  | MVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_PF | #2MTR 功率因素 | DTR | S76//2MTR/PF |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_MVA | #3MTR二次側 MVA | DTR | S76//3MTR/MVA |  | MVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_PF | #3MTR 功率因素 | DTR | S76//3MTR/PF |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_MVA | #4MTR二次側 MVA | DTR | S76//4MTR/MVA |  | MVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_PF | #4MTR 功率因素 | DTR | S76//4MTR/PF |  | RPDC_PF_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_MVA | #5MTR二次側 MVA | DTR | S76//5MTR/MVA |  | MVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_PF | #5MTR 功率因素 | DTR | S76//5MTR/PF |  | RPDC_PF_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S76 | 佳里一SS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.210_SC_MVAR | 11KV#1SC MVAR | SC | S76/11/210/MVAR |  | SC_CAL_11 |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.220_SC_MVAR | 11KV#2SC MVAR | SC | S76/11/220/MVAR |  | SC_CAL_11 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.230_SC_MVAR | 11KV#3SC MVAR | SC | S76/11/230/MVAR |  | SC_CAL_11 |  |  | 60 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.240_SC_MVAR | 11KV#4SC MVAR | SC | S76/11/240/MVAR |  | SC_CAL_11 |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.250_SC_MVAR | 11KV#5SC MVAR | SC | S76/11/250/MVAR |  | SC_CAL_11 |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 69 | 69kV | 810_SC | #1SC | 10.8 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.810_SC_MVAR | 69KV#1SC MVAR | SC | S76/69/810/MVAR |  | SC_CAL_69 |  |  | 63 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | I | [25 empty] | ADCS_N | [8 empty] | 佳一SS.650_AMP | 佳里麻豆線 AMP | LINE69 | S76/69/650/I |  | AMP_CAL |  |  | 64 | CalcAIPoint | [21 empty] | C12R0960 | 864.000000 | 864.000000 | 960.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳25線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳25線KVA | 11KV佳25線KVA | FEEDER |  |  | KVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳25線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳25線KW | 11KV佳25線KW | FEEDER |  |  | KW_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳30線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳30線KVA | 11KV佳30線KVA | FEEDER |  |  | KVA_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳30線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳30線KW | 11KV佳30線KW | FEEDER |  |  | KW_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳45線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳45線KVA | 11KV佳45線KVA | FEEDER |  |  | KVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 佳45線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.佳45線KW | 11KV佳45線KW | FEEDER |  |  | KW_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | I | [25 empty] | ADCS_N | [8 empty] | 佳一SS.730_AMP | 學甲佳里一路 AMP | LINE69 | S76/69/730/I |  | AMP_CAL |  |  | 71 | CalcAIPoint | [21 empty] | C12R0831 | 747.900024 | 747.900024 | 831.000000 | 1200.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
S76 | 佳里一SS | 0 |  |  |  |  | 備01線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.備01線KVA | 11KV備01線KVA | FEEDER |  |  | KVA_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 備01線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.備01線KW | 11KV備01線KW | FEEDER |  |  | KW_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 備02線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.備02線KVA | 11KV備02線KVA | FEEDER |  |  | KVA_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 0 |  |  |  |  | 備02線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.備02線KW | 11KV備02線KW | FEEDER |  |  | KW_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 69 | 69kV | 620_CB | 學甲佳里二路(620_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.620_CB_4 | 620(學甲佳里二路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 810_CB | #1SC(810_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.810_CB_4 | 810(69KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 78 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 79 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_N | [8 empty] | 佳一SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 80 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_N | [8 empty] | 佳一SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 81 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 佳里變電所重故障點燈 | 佳里變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 佳一SS.變電所重故障 | 佳里變電所重故障點燈 (AD) | OTHER | S76/0/CalcPoint/SUBA |  | STATION_FAULT_20 |  |  | 82 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 變電所重故障 | 佳里變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.變電所重故障_4 | 佳里變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 83 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 變電所輕故障 | 佳里變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.變電所輕故障_4 | 佳里變電所輕故障點燈 (D4) | OTHER |  |  | STATION_FAULT_7 |  |  | 84 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620_AMP | 學甲佳里二路 | [27 empty] | ADCS_N | [8 empty] | 佳一SS.620_AMP_A | 學甲佳里二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620_AMP | 學甲佳里二路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.620_AMP_4 | 學甲佳里二路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR_MVA | #1MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_MVA_4 | #1MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR_MVA | #2MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_MVA_4 | #2MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR_MVA | #3MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_MVA_4 | #3MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR_MVA | #4MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_MVA_4 | #4MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR_MVA | #5MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_MVA_4 | #5MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_PERM | #5MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650_AMP | 佳里麻豆線 | [27 empty] | ADCS_N | [8 empty] | 佳一SS.650_AMP_A | 佳里麻豆線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650_AMP | 佳里麻豆線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.650_AMP_4 | 佳里麻豆線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650_CB | 佳里麻豆線(650_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.650_CB_4 | 650(佳里麻豆線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 99 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 730_AMP | 學甲佳里一路 | [27 empty] | ADCS_N | [8 empty] | 佳一SS.730_AMP_A | 學甲佳里一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730_AMP | 學甲佳里一路 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.730_AMP_4 | 學甲佳里一路 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730_CB | 學甲佳里一路(730_CB) |  | 4 | [25 empty] | 69KV_N | [8 empty] | 佳一SS.730_CB_4 | 730(學甲佳里一路) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 102 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | _IED_CFA | IED通訊故障 | [27 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_IED_CFA_A | 69KV IED通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 103 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | _IED_FA | IED故障 | [27 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_IED_FA_A | 69KV IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 104 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_S | [8 empty] | 佳一SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 105 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 600_CB | 600(600_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.600_CB_4 | 600 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 106 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 600GDA(1) | #1BUS | [27 empty] | ADCS_N | [8 empty] | 佳一SS.600GDA(1)_A | 69KV #1BUS TIE(600) 67N (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 107 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600GDA(2) | #2BUS | [27 empty] | ADCS_N | [8 empty] | 佳一SS.600GDA(2)_A | 69KV #2BUS TIE(600) 67N (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 108 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600PHA(1) | #1BUS | [27 empty] | ADCS_N | [8 empty] | 佳一SS.600PHA(1)_A | 69KV #1BUS TIE(600) 67 (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 109 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600PHA(2) | #2BUS | [27 empty] | ADCS_N | [8 empty] | 佳一SS.600PHA(2)_A | 69KV #2BUS TIE(600) 67 (AD) | OTHER |  |  | AD_LAMP_DD_5 |  |  | 110 | CalcDIPoint | [38 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S76/0/RTU/ADCH1 |  |  |  | CDC | 111 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S76/0/RTU/ADCH2 |  |  |  | CDC | 112 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | S76/0/RTU/ADCH3 |  |  |  | CDC | 113 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | S76/0/RTU/ADCH4 |  |  |  | CDC | 114 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S76/0/RTU/ADCL1 |  |  |  | CDC | 115 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S76/0/RTU/ADCL2 |  |  |  | CDC | 116 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | S76/0/RTU/ADCL3 |  |  |  | CDC | 117 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | S76/0/RTU/ADCL4 |  |  |  | CDC | 118 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-8C | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | S76/69/1BUS/V |  |  |  | CDC | 119 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S76 | 佳里一SS | 11 | 11kV | 1BUS | #1BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV#1BUS_KV | 11KV #1BUS KV | BUS | S76/11/1BUS/V_R |  |  |  | CDC | 120 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 3BUS | #3BUS |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV#3BUS_KV | 11KV #3BUS KV | BUS | S76/11/3BUS/V_R |  |  |  | CDC | 121 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 4BUS | #4BUS |  | V | [17 empty] | 2-89 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV#4BUS_KV | 11KV #4BUS KV | BUS | S76/11/4BUS/V_R |  |  |  | CDC | 122 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 5BUS | #5BUS |  | V | [17 empty] | 2-AD | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV#5BUS_KV | 11KV #5BUS KV | BUS | S76/11/5BUS/V_R |  |  |  | CDC | 123 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.620_MW | 學甲佳里二路 MW | LINE69 | S76/69/620/MW |  |  |  | CDC | 124 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.620_MVAR | 學甲佳里二路 MVAR | LINE69 | S76/69/620/MVAR |  |  |  | CDC | 125 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 七股線 | 七股線 |  | 七股線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.七股線KVAR | 11KV七股線 KVAR | FEEDER | S76/11/KN28/KVAR |  |  |  | CDC | 126 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 七股線 | 七股線 |  | 七股線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.七股線A1 | 11KV七股線 R相AMP | FEEDER | S76/11/KN28/I_R |  |  |  | CDC | 127 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 七股線 | 七股線 |  | 七股線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.七股線A2 | 11KV七股線 S相AMP | FEEDER | S76/11/KN28/I_S |  |  |  | CDC | 128 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 七股線 | 七股線 |  | 七股線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.七股線A3 | 11KV七股線 T相AMP | FEEDER | S76/11/KN28/I_T |  |  |  | CDC | 129 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 七股線 | 七股線 |  | 七股線A0 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.七股線A0 | 11KV七股線 N相AMP | FEEDER | S76/11/KN28/I_N |  |  |  | CDC | 130 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 三股線 | 三股線 |  | 三股線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.三股線KVAR | 11KV三股線 KVAR | FEEDER | S76/11/KN36/KVAR |  |  |  | CDC | 131 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 三股線 | 三股線 |  | 三股線A1 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.三股線A1 | 11KV三股線 R相AMP | FEEDER | S76/11/KN36/I_R |  |  |  | CDC | 132 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 三股線 | 三股線 |  | 三股線A2 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.三股線A2 | 11KV三股線 S相AMP | FEEDER | S76/11/KN36/I_S |  |  |  | CDC | 133 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 三股線 | 三股線 |  | 三股線A3 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.三股線A3 | 11KV三股線 T相AMP | FEEDER | S76/11/KN36/I_T |  |  |  | CDC | 134 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 三股線 | 三股線 |  | 三股線A0 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.三股線A0 | 11KV三股線 N相AMP | FEEDER | S76/11/KN36/I_N |  |  |  | CDC | 135 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 子良線 | 子良線 |  | 子良線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.子良線KVAR | 11KV子良線 KVAR | FEEDER | S76/11/KN32/KVAR |  |  |  | CDC | 136 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 子良線 | 子良線 |  | 子良線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.子良線A1 | 11KV子良線 R相AMP | FEEDER | S76/11/KN32/I_R |  |  |  | CDC | 137 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 子良線 | 子良線 |  | 子良線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.子良線A2 | 11KV子良線 S相AMP | FEEDER | S76/11/KN32/I_S |  |  |  | CDC | 138 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 子良線 | 子良線 |  | 子良線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.子良線A3 | 11KV子良線 T相AMP | FEEDER | S76/11/KN32/I_T |  |  |  | CDC | 139 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 子良線 | 子良線 |  | 子良線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.子良線A0 | 11KV子良線 N相AMP | FEEDER | S76/11/KN32/I_N |  |  |  | CDC | 140 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 中山線 | 中山線 |  | 中山線KVAR | [17 empty] | 2-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.中山線KVAR | 11KV中山線 KVAR | FEEDER | S76/11/KN42/KVAR |  |  |  | CDC | 141 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 中山線 | 中山線 |  | 中山線A1 | [17 empty] | 2-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.中山線A1 | 11KV中山線 R相AMP | FEEDER | S76/11/KN42/I_R |  |  |  | CDC | 142 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 中山線 | 中山線 |  | 中山線A2 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.中山線A2 | 11KV中山線 S相AMP | FEEDER | S76/11/KN42/I_S |  |  |  | CDC | 143 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 中山線 | 中山線 |  | 中山線A3 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.中山線A3 | 11KV中山線 T相AMP | FEEDER | S76/11/KN42/I_T |  |  |  | CDC | 144 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 中山線 | 中山線 |  | 中山線A0 | [17 empty] | 2-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.中山線A0 | 11KV中山線 N相AMP | FEEDER | S76/11/KN42/I_N |  |  |  | CDC | 145 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 仁愛線 | 仁愛線 |  | 仁愛線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.仁愛線KVAR | 11KV仁愛線 KVAR | FEEDER | S76/11/KN40/KVAR |  |  |  | CDC | 146 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 仁愛線 | 仁愛線 |  | 仁愛線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.仁愛線A1 | 11KV仁愛線 R相AMP | FEEDER | S76/11/KN40/I_R |  |  |  | CDC | 147 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 仁愛線 | 仁愛線 |  | 仁愛線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.仁愛線A2 | 11KV仁愛線 S相AMP | FEEDER | S76/11/KN40/I_S |  |  |  | CDC | 148 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 仁愛線 | 仁愛線 |  | 仁愛線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.仁愛線A3 | 11KV仁愛線 T相AMP | FEEDER | S76/11/KN40/I_T |  |  |  | CDC | 149 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 仁愛線 | 仁愛線 |  | 仁愛線A0 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.仁愛線A0 | 11KV仁愛線 N相AMP | FEEDER | S76/11/KN40/I_N |  |  |  | CDC | 150 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 北農線 | 北農線 |  | 北農線KVAR | [17 empty] | 2-BA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.北農線KVAR | 11KV北農線 KVAR | FEEDER | S76/11/KN41/KVAR |  |  |  | CDC | 151 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 北農線 | 北農線 |  | 北農線A1 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.北農線A1 | 11KV北農線 R相AMP | FEEDER | S76/11/KN41/I_R |  |  |  | CDC | 152 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 北農線 | 北農線 |  | 北農線A2 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.北農線A2 | 11KV北農線 S相AMP | FEEDER | S76/11/KN41/I_S |  |  |  | CDC | 153 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 北農線 | 北農線 |  | 北農線A3 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.北農線A3 | 11KV北農線 T相AMP | FEEDER | S76/11/KN41/I_T |  |  |  | CDC | 154 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 北農線 | 北農線 |  | 北農線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.北農線A0 | 11KV北農線 N相AMP | FEEDER | S76/11/KN41/I_N |  |  |  | CDC | 155 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 光復線 | 光復線 |  | 光復線KVAR | [17 empty] | 2-9A | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.光復線KVAR | 11KV光復線 KVAR | FEEDER | S76/11/KN38/KVAR |  |  |  | CDC | 156 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 光復線 | 光復線 |  | 光復線A1 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.光復線A1 | 11KV光復線 R相AMP | FEEDER | S76/11/KN38/I_R |  |  |  | CDC | 157 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 光復線 | 光復線 |  | 光復線A2 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.光復線A2 | 11KV光復線 S相AMP | FEEDER | S76/11/KN38/I_S |  |  |  | CDC | 158 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 光復線 | 光復線 |  | 光復線A3 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.光復線A3 | 11KV光復線 T相AMP | FEEDER | S76/11/KN38/I_T |  |  |  | CDC | 159 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 光復線 | 光復線 |  | 光復線A0 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.光復線A0 | 11KV光復線 N相AMP | FEEDER | S76/11/KN38/I_N |  |  |  | CDC | 160 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 西港線 | 西港線 |  | 西港線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.西港線KVAR | 11KV西港線 KVAR | FEEDER | S76/11/KN31/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 西港線 | 西港線 |  | 西港線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.西港線A1 | 11KV西港線 R相AMP | FEEDER | S76/11/KN31/I_R |  |  |  | CDC | 162 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 西港線 | 西港線 |  | 西港線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.西港線A2 | 11KV西港線 S相AMP | FEEDER | S76/11/KN31/I_S |  |  |  | CDC | 163 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 西港線 | 西港線 |  | 西港線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.西港線A3 | 11KV西港線 T相AMP | FEEDER | S76/11/KN31/I_T |  |  |  | CDC | 164 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 西港線 | 西港線 |  | 西港線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.西港線A0 | 11KV西港線 N相AMP | FEEDER | S76/11/KN31/I_N |  |  |  | CDC | 165 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳工線 | 佳工線 |  | 佳工線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳工線KVAR | 11KV佳工線 KVAR | FEEDER | S76/11/KN23/KVAR |  |  |  | CDC | 166 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳工線 | 佳工線 |  | 佳工線A1 | [17 empty] | 1-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳工線A1 | 11KV佳工線 R相AMP | FEEDER | S76/11/KN23/I_R |  |  |  | CDC | 167 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳工線 | 佳工線 |  | 佳工線A2 | [17 empty] | 1-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳工線A2 | 11KV佳工線 S相AMP | FEEDER | S76/11/KN23/I_S |  |  |  | CDC | 168 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳工線 | 佳工線 |  | 佳工線A3 | [17 empty] | 1-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳工線A3 | 11KV佳工線 T相AMP | FEEDER | S76/11/KN23/I_T |  |  |  | CDC | 169 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳工線 | 佳工線 |  | 佳工線A0 | [17 empty] | 1-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳工線A0 | 11KV佳工線 N相AMP | FEEDER | S76/11/KN23/I_N |  |  |  | CDC | 170 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳西線 | 佳西線 |  | 佳西線KVAR | [17 empty] | 2-C8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳西線KVAR | 11KV佳西線 KVAR | FEEDER | S76/11/KN44/KVAR |  |  |  | CDC | 171 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳西線 | 佳西線 |  | 佳西線A1 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳西線A1 | 11KV佳西線 R相AMP | FEEDER | S76/11/KN44/I_R |  |  |  | CDC | 172 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳西線 | 佳西線 |  | 佳西線A2 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳西線A2 | 11KV佳西線 S相AMP | FEEDER | S76/11/KN44/I_S |  |  |  | CDC | 173 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳西線 | 佳西線 |  | 佳西線A3 | [17 empty] | 2-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳西線A3 | 11KV佳西線 T相AMP | FEEDER | S76/11/KN44/I_T |  |  |  | CDC | 174 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳西線 | 佳西線 |  | 佳西線A0 | [17 empty] | 2-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳西線A0 | 11KV佳西線 N相AMP | FEEDER | S76/11/KN44/I_N |  |  |  | CDC | 175 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳麻線 | 佳麻線 |  | 佳麻線KVAR | [17 empty] | 2-C4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳麻線KVAR | 11KV佳麻線 KVAR | FEEDER | S76/11/KN43/KVAR |  |  |  | CDC | 176 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳麻線 | 佳麻線 |  | 佳麻線A1 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳麻線A1 | 11KV佳麻線 R相AMP | FEEDER | S76/11/KN43/I_R |  |  |  | CDC | 177 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳麻線 | 佳麻線 |  | 佳麻線A2 | [17 empty] | 2-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳麻線A2 | 11KV佳麻線 S相AMP | FEEDER | S76/11/KN43/I_S |  |  |  | CDC | 178 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳麻線 | 佳麻線 |  | 佳麻線A3 | [17 empty] | 2-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳麻線A3 | 11KV佳麻線 T相AMP | FEEDER | S76/11/KN43/I_T |  |  |  | CDC | 179 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳麻線 | 佳麻線 |  | 佳麻線A0 | [17 empty] | 2-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳麻線A0 | 11KV佳麻線 N相AMP | FEEDER | S76/11/KN43/I_N |  |  |  | CDC | 180 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳塭線 | 佳塭線 |  | 佳塭線KVAR | [17 empty] | 2-96 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳塭線KVAR | 11KV佳塭線 KVAR | FEEDER | S76/11/KN37/KVAR |  |  |  | CDC | 181 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳塭線 | 佳塭線 |  | 佳塭線A1 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳塭線A1 | 11KV佳塭線 R相AMP | FEEDER | S76/11/KN37/I_R |  |  |  | CDC | 182 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳塭線 | 佳塭線 |  | 佳塭線A2 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳塭線A2 | 11KV佳塭線 S相AMP | FEEDER | S76/11/KN37/I_S |  |  |  | CDC | 183 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳塭線 | 佳塭線 |  | 佳塭線A3 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳塭線A3 | 11KV佳塭線 T相AMP | FEEDER | S76/11/KN37/I_T |  |  |  | CDC | 184 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳塭線 | 佳塭線 |  | 佳塭線A0 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳塭線A0 | 11KV佳塭線 N相AMP | FEEDER | S76/11/KN37/I_N |  |  |  | CDC | 185 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳興線 | 佳興線 |  | 佳興線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳興線KVAR | 11KV佳興線 KVAR | FEEDER | S76/11/KN22/KVAR |  |  |  | CDC | 186 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳興線 | 佳興線 |  | 佳興線A1 | [17 empty] | 1-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳興線A1 | 11KV佳興線 R相AMP | FEEDER | S76/11/KN22/I_R |  |  |  | CDC | 187 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳興線 | 佳興線 |  | 佳興線A2 | [17 empty] | 1-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳興線A2 | 11KV佳興線 S相AMP | FEEDER | S76/11/KN22/I_S |  |  |  | CDC | 188 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳興線 | 佳興線 |  | 佳興線A3 | [17 empty] | 1-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳興線A3 | 11KV佳興線 T相AMP | FEEDER | S76/11/KN22/I_T |  |  |  | CDC | 189 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳興線 | 佳興線 |  | 佳興線A0 | [17 empty] | 1-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳興線A0 | 11KV佳興線 N相AMP | FEEDER | S76/11/KN22/I_N |  |  |  | CDC | 190 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 林樂線 | 林樂線 |  | 林樂線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.林樂線KVAR | 11KV林樂線 KVAR | FEEDER | S76/11/KN35/KVAR |  |  |  | CDC | 191 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 林樂線 | 林樂線 |  | 林樂線A1 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.林樂線A1 | 11KV林樂線 R相AMP | FEEDER | S76/11/KN35/I_R |  |  |  | CDC | 192 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 林樂線 | 林樂線 |  | 林樂線A2 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.林樂線A2 | 11KV林樂線 S相AMP | FEEDER | S76/11/KN35/I_S |  |  |  | CDC | 193 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 林樂線 | 林樂線 |  | 林樂線A3 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.林樂線A3 | 11KV林樂線 T相AMP | FEEDER | S76/11/KN35/I_T |  |  |  | CDC | 194 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 林樂線 | 林樂線 |  | 林樂線A0 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.林樂線A0 | 11KV林樂線 N相AMP | FEEDER | S76/11/KN35/I_N |  |  |  | CDC | 195 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 通吉線 | 通吉線 |  | 通吉線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.通吉線KVAR | 11KV通吉線 KVAR | FEEDER | S76/11/KN24/KVAR |  |  |  | CDC | 196 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 通吉線 | 通吉線 |  | 通吉線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.通吉線A1 | 11KV通吉線 R相AMP | FEEDER | S76/11/KN24/I_R |  |  |  | CDC | 197 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 通吉線 | 通吉線 |  | 通吉線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.通吉線A2 | 11KV通吉線 S相AMP | FEEDER | S76/11/KN24/I_S |  |  |  | CDC | 198 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 通吉線 | 通吉線 |  | 通吉線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.通吉線A3 | 11KV通吉線 T相AMP | FEEDER | S76/11/KN24/I_T |  |  |  | CDC | 199 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 通吉線 | 通吉線 |  | 通吉線A0 | [17 empty] | 1-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.通吉線A0 | 11KV通吉線 N相AMP | FEEDER | S76/11/KN24/I_N |  |  |  | CDC | 200 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 頂城線 | 頂城線 |  | 頂城線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.頂城線KVAR | 11KV頂城線 KVAR | FEEDER | S76/11/KN27/KVAR |  |  |  | CDC | 201 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 頂城線 | 頂城線 |  | 頂城線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.頂城線A1 | 11KV頂城線 R相AMP | FEEDER | S76/11/KN27/I_R |  |  |  | CDC | 202 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 頂城線 | 頂城線 |  | 頂城線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.頂城線A2 | 11KV頂城線 S相AMP | FEEDER | S76/11/KN27/I_S |  |  |  | CDC | 203 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 頂城線 | 頂城線 |  | 頂城線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.頂城線A3 | 11KV頂城線 T相AMP | FEEDER | S76/11/KN27/I_T |  |  |  | CDC | 204 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 頂城線 | 頂城線 |  | 頂城線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.頂城線A0 | 11KV頂城線 N相AMP | FEEDER | S76/11/KN27/I_N |  |  |  | CDC | 205 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 塭寮線 | 塭寮線 |  | 塭寮線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.塭寮線KVAR | 11KV塭寮線 KVAR | FEEDER | S76/11/KN29/KVAR |  |  |  | CDC | 206 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 塭寮線 | 塭寮線 |  | 塭寮線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.塭寮線A1 | 11KV塭寮線 R相AMP | FEEDER | S76/11/KN29/I_R |  |  |  | CDC | 207 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 塭寮線 | 塭寮線 |  | 塭寮線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.塭寮線A2 | 11KV塭寮線 S相AMP | FEEDER | S76/11/KN29/I_S |  |  |  | CDC | 208 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 塭寮線 | 塭寮線 |  | 塭寮線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.塭寮線A3 | 11KV塭寮線 T相AMP | FEEDER | S76/11/KN29/I_T |  |  |  | CDC | 209 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 塭寮線 | 塭寮線 |  | 塭寮線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.塭寮線A0 | 11KV塭寮線 N相AMP | FEEDER | S76/11/KN29/I_N |  |  |  | CDC | 210 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.新生線KVAR | 11KV新生線 KVAR | FEEDER | S76/11/KN39/KVAR |  |  |  | CDC | 211 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A1 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.新生線A1 | 11KV新生線 R相AMP | FEEDER | S76/11/KN39/I_R |  |  |  | CDC | 212 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A2 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.新生線A2 | 11KV新生線 S相AMP | FEEDER | S76/11/KN39/I_S |  |  |  | CDC | 213 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A3 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.新生線A3 | 11KV新生線 T相AMP | FEEDER | S76/11/KN39/I_T |  |  |  | CDC | 214 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 新生線 | 新生線 |  | 新生線A0 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.新生線A0 | 11KV新生線 N相AMP | FEEDER | S76/11/KN39/I_N |  |  |  | CDC | 215 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 嘉福線 | 嘉福線 |  | 嘉福線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.嘉福線KVAR | 11KV嘉福線 KVAR | FEEDER | S76/11/KN33/KVAR |  |  |  | CDC | 216 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 嘉福線 | 嘉福線 |  | 嘉福線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.嘉福線A1 | 11KV嘉福線 R相AMP | FEEDER | S76/11/KN33/I_R |  |  |  | CDC | 217 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 嘉福線 | 嘉福線 |  | 嘉福線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.嘉福線A2 | 11KV嘉福線 S相AMP | FEEDER | S76/11/KN33/I_S |  |  |  | CDC | 218 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 嘉福線 | 嘉福線 |  | 嘉福線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.嘉福線A3 | 11KV嘉福線 T相AMP | FEEDER | S76/11/KN33/I_T |  |  |  | CDC | 219 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 嘉福線 | 嘉福線 |  | 嘉福線A0 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.嘉福線A0 | 11KV嘉福線 N相AMP | FEEDER | S76/11/KN33/I_N |  |  |  | CDC | 220 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漳洲線 | 漳洲線 |  | 漳洲線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漳洲線KVAR | 11KV漳洲線 KVAR | FEEDER | S76/11/KN26/KVAR |  |  |  | CDC | 221 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漳洲線 | 漳洲線 |  | 漳洲線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漳洲線A1 | 11KV漳洲線 R相AMP | FEEDER | S76/11/KN26/I_R |  |  |  | CDC | 222 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漳洲線 | 漳洲線 |  | 漳洲線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漳洲線A2 | 11KV漳洲線 S相AMP | FEEDER | S76/11/KN26/I_S |  |  |  | CDC | 223 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漳洲線 | 漳洲線 |  | 漳洲線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漳洲線A3 | 11KV漳洲線 T相AMP | FEEDER | S76/11/KN26/I_T |  |  |  | CDC | 224 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漳洲線 | 漳洲線 |  | 漳洲線A0 | [17 empty] | 1-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漳洲線A0 | 11KV漳洲線 N相AMP | FEEDER | S76/11/KN26/I_N |  |  |  | CDC | 225 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 篤加線 | 篤加線 |  | 篤加線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.篤加線KVAR | 11KV篤加線 KVAR | FEEDER | S76/11/KN34/KVAR |  |  |  | CDC | 226 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 篤加線 | 篤加線 |  | 篤加線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.篤加線A1 | 11KV篤加線 R相AMP | FEEDER | S76/11/KN34/I_R |  |  |  | CDC | 227 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 篤加線 | 篤加線 |  | 篤加線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.篤加線A2 | 11KV篤加線 S相AMP | FEEDER | S76/11/KN34/I_S |  |  |  | CDC | 228 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 篤加線 | 篤加線 |  | 篤加線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.篤加線A3 | 11KV篤加線 T相AMP | FEEDER | S76/11/KN34/I_T |  |  |  | CDC | 229 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 篤加線 | 篤加線 |  | 篤加線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.篤加線A0 | 11KV篤加線 N相AMP | FEEDER | S76/11/KN34/I_N |  |  |  | CDC | 230 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漚汪線 | 漚汪線 |  | 漚汪線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漚汪線KVAR | 11KV漚汪線 KVAR | FEEDER | S76/11/KN21/KVAR |  |  |  | CDC | 231 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漚汪線 | 漚汪線 |  | 漚汪線A1 | [17 empty] | 1-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漚汪線A1 | 11KV漚汪線 R相AMP | FEEDER | S76/11/KN21/I_R |  |  |  | CDC | 232 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漚汪線 | 漚汪線 |  | 漚汪線A2 | [17 empty] | 1-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漚汪線A2 | 11KV漚汪線 S相AMP | FEEDER | S76/11/KN21/I_S |  |  |  | CDC | 233 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漚汪線 | 漚汪線 |  | 漚汪線A3 | [17 empty] | 1-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漚汪線A3 | 11KV漚汪線 T相AMP | FEEDER | S76/11/KN21/I_T |  |  |  | CDC | 234 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 漚汪線 | 漚汪線 |  | 漚汪線A0 | [17 empty] | 1-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.漚汪線A0 | 11KV漚汪線 N相AMP | FEEDER | S76/11/KN21/I_N |  |  |  | CDC | 235 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE1 | #2B-#1 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE1_A1 | 11KV #2B-#1 TIE R相AMP | TIE | S76/11/TIE1/I_R |  |  |  | CDC | 236 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE1 | #2B-#1 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE1_A2 | 11KV #2B-#1 TIE S相AMP | TIE | S76/11/TIE1/I_S |  |  |  | CDC | 237 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE1 | #2B-#1 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE1_A3 | 11KV #2B-#1 TIE T相AMP | TIE | S76/11/TIE1/I_T |  |  |  | CDC | 238 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE2 | #3-#2A |  | I_R | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE2_A1 | 11KV #3-#2A TIE R相AMP | TIE | S76/11/TIE2/I_R |  |  |  | CDC | 239 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE2 | #3-#2A |  | I_S | [17 empty] | 1-DC | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE2_A2 | 11KV #3-#2A TIE S相AMP | TIE | S76/11/TIE2/I_S |  |  |  | CDC | 240 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE2 | #3-#2A |  | I_T | [17 empty] | 1-DD | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE2_A3 | 11KV #3-#2A TIE T相AMP | TIE | S76/11/TIE2/I_T |  |  |  | CDC | 241 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE3 | TIE3 |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE3_A1 | 11KV TIE3 R相AMP | TIE | S76/11/TIE3/I_R |  |  |  | CDC | 242 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE3 | TIE3 |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE3_A2 | 11KV TIE3 S相AMP | TIE | S76/11/TIE3/I_S |  |  |  | CDC | 243 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE3 | TIE3 |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE3_A3 | 11KV TIE3 T相AMP | TIE | S76/11/TIE3/I_T |  |  |  | CDC | 244 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE4 | #4-#5 |  | I_R | [17 empty] | 2-A6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE4_A1 | 11KV #4-#5 TIE R相AMP | TIE | S76/11/TIE4/I_R |  |  |  | CDC | 245 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE4 | #4-#5 |  | I_S | [17 empty] | 2-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE4_A2 | 11KV #4-#5 TIE S相AMP | TIE | S76/11/TIE4/I_S |  |  |  | CDC | 246 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE4 | #4-#5 |  | I_T | [17 empty] | 2-A8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE4_A3 | 11KV #4-#5 TIE T相AMP | TIE | S76/11/TIE4/I_T |  |  |  | CDC | 247 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE5 | TIE5 |  | I_R | [17 empty] | 2-D7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE5_A1 | 11KV TIE5 R相AMP | TIE | S76/11/TIE5/I_R |  |  |  | CDC | 248 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE5 | TIE5 |  | I_S | [17 empty] | 2-D8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE5_A2 | 11KV TIE5 S相AMP | TIE | S76/11/TIE5/I_S |  |  |  | CDC | 249 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | _TIE5 | TIE5 |  | I_T | [17 empty] | 2-D9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV_TIE5_A3 | 11KV TIE5 T相AMP | TIE | S76/11/TIE5/I_T |  |  |  | CDC | 250 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_MW | #1MTR二次側 MW | DTR | S76/11/M1/MW |  |  |  | CDC | 251 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_MVAR | #1MTR二次側 MVAR | DTR | S76/11/M1/MVAR |  |  |  | CDC | 252 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_A1 | #1MTR二次側 R相AMP | DTR | S76/11/M1/I_R |  |  |  | CDC | 253 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_A2 | #1MTR二次側 S相AMP | DTR | S76/11/M1/I_S |  |  |  | CDC | 254 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_A3 | #1MTR二次側 T相AMP | DTR | S76/11/M1/I_T |  |  |  | CDC | 255 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_OIL | #1MTR 油溫 | DTR | S76//1MTR/OilTemp |  |  |  | CDC | 256 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_COIL | #1MTR 線溫 | DTR | S76//1MTR/CoilTemp |  |  |  | CDC | 257 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_TAP | #1MTR OLTC TAP | DTR | S76//1MTR/TapPosMv |  |  |  | CDC | 258 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.500000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_MW | #2MTR二次側 MW | DTR | S76/11/M2A/MW |  |  |  | CDC | 259 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_MVAR | #2MTR二次側 MVAR | DTR | S76/11/M2A/MVAR |  |  |  | CDC | 260 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_A1 | #2MTR二次側 R相AMP | DTR | S76/11/M2A/I_R |  |  |  | CDC | 261 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_A2 | #2MTR二次側 S相AMP | DTR | S76/11/M2A/I_S |  |  |  | CDC | 262 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_A3 | #2MTR二次側 T相AMP | DTR | S76/11/M2A/I_T |  |  |  | CDC | 263 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_OIL | #2MTR 油溫 | DTR | S76//2MTR/OilTemp |  |  |  | CDC | 264 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_COIL | #2MTR 線溫 | DTR | S76//2MTR/CoilTemp |  |  |  | CDC | 265 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_TAP | #2MTR OLTC TAP | DTR | S76//2MTR/TapPosMv |  |  |  | CDC | 266 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_MW | #3MTR二次側 MW | DTR | S76/11/M3/MW |  |  |  | CDC | 267 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_MVAR | #3MTR二次側 MVAR | DTR | S76/11/M3/MVAR |  |  |  | CDC | 268 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR二次側 |  | I_R | [17 empty] | 1-E8 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_A1 | #3MTR二次側 R相AMP | DTR | S76/11/M3/I_R |  |  |  | CDC | 269 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR二次側 |  | I_S | [17 empty] | 1-E9 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_A2 | #3MTR二次側 S相AMP | DTR | S76/11/M3/I_S |  |  |  | CDC | 270 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR二次側 |  | I_T | [17 empty] | 1-EA | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_A3 | #3MTR二次側 T相AMP | DTR | S76/11/M3/I_T |  |  |  | CDC | 271 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-E4 | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_OIL | #3MTR 油溫 | DTR | S76//3MTR/OilTemp |  |  |  | CDC | 272 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-E3 | [5 empty] | COIL_-150_150(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_COIL | #3MTR 線溫 | DTR | S76//3MTR/CoilTemp |  |  |  | CDC | 273 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-E5 |  | 1-62 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_TAP | #3MTR OLTC TAP | DTR | S76//3MTR/TapPosMv |  |  |  | CDC | 274 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR二次側 |  | MW | [17 empty] | 2-8D | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_MW | #4MTR二次側 MW | DTR | S76/11/M4/MW |  |  |  | CDC | 275 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR二次側 |  | MVAR | [17 empty] | 2-8E | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_MVAR | #4MTR二次側 MVAR | DTR | S76/11/M4/MVAR |  |  |  | CDC | 276 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR二次側 |  | I_R | [17 empty] | 2-8F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_A1 | #4MTR二次側 R相AMP | DTR | S76/11/M4/I_R |  |  |  | CDC | 277 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR二次側 |  | I_S | [17 empty] | 2-90 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_A2 | #4MTR二次側 S相AMP | DTR | S76/11/M4/I_S |  |  |  | CDC | 278 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR二次側 |  | I_T | [17 empty] | 2-91 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_A3 | #4MTR二次側 T相AMP | DTR | S76/11/M4/I_T |  |  |  | CDC | 279 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | OilTemp | [17 empty] | 2-8B | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_OIL | #4MTR 油溫 | DTR | S76//4MTR/OilTemp |  |  |  | CDC | 280 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | CoilTemp | [17 empty] | 2-8A | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_COIL | #4MTR 線溫 | DTR | S76//4MTR/CoilTemp |  |  |  | CDC | 281 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | TapPosMv | [17 empty] | 2-8C |  | 1-76 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_TAP | #4MTR OLTC TAP | DTR | S76//4MTR/TapPosMv |  |  |  | CDC | 282 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR二次側 |  | MW | [17 empty] | 2-B1 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_MW | #5MTR二次側 MW | DTR | S76/11/M5/MW |  |  |  | CDC | 283 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR二次側 |  | MVAR | [17 empty] | 2-B2 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_MVAR | #5MTR二次側 MVAR | DTR | S76/11/M5/MVAR |  |  |  | CDC | 284 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR二次側 |  | I_R | [17 empty] | 2-B3 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_A1 | #5MTR二次側 R相AMP | DTR | S76/11/M5/I_R |  |  |  | CDC | 285 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR二次側 |  | I_S | [17 empty] | 2-B4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_A2 | #5MTR二次側 S相AMP | DTR | S76/11/M5/I_S |  |  |  | CDC | 286 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR二次側 |  | I_T | [17 empty] | 2-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_A3 | #5MTR二次側 T相AMP | DTR | S76/11/M5/I_T |  |  |  | CDC | 287 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | OilTemp | [17 empty] | 2-AF | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_OIL | #5MTR 油溫 | DTR | S76//5MTR/OilTemp |  |  |  | CDC | 288 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | CoilTemp | [17 empty] | 2-AE | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_COIL | #5MTR 線溫 | DTR | S76//5MTR/CoilTemp |  |  |  | CDC | 289 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | TapPosMv | [17 empty] | 2-B0 |  | 2-09 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_TAP | #5MTR OLTC TAP | DTR | S76//5MTR/TapPosMv |  |  |  | CDC | 290 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S76 | 佳里一SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.直流電源電壓 | 直流電源電壓 | OTHER | S76/0/StaDev/DCV |  |  |  | CDC | 291 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.650_MW | 佳里麻豆線 MW | LINE69 | S76/69/650/MW |  |  |  | CDC | 292 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.650_MVAR | 佳里麻豆線 MVAR | LINE69 | S76/69/650/MVAR |  |  |  | CDC | 293 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳25線 | 佳25線 |  | 佳25線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳25線KVAR | 11KV佳25線 KVAR | FEEDER | S76/11/KN25/KVAR |  |  |  | CDC | 294 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳25線 | 佳25線 |  | 佳25線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳25線A1 | 11KV佳25線 R相AMP | FEEDER | S76/11/KN25/I_R |  |  |  | CDC | 295 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳25線 | 佳25線 |  | 佳25線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳25線A2 | 11KV佳25線 S相AMP | FEEDER | S76/11/KN25/I_S |  |  |  | CDC | 296 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳25線 | 佳25線 |  | 佳25線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳25線A3 | 11KV佳25線 T相AMP | FEEDER | S76/11/KN25/I_T |  |  |  | CDC | 297 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳25線 | 佳25線 |  | 佳25線A0 | [17 empty] | 1-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳25線A0 | 11KV佳25線 N相AMP | FEEDER | S76/11/KN25/I_N |  |  |  | CDC | 298 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳30線 | 佳30線 |  | 佳30線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳30線KVAR | 11KV佳30線 KVAR | FEEDER | S76/11/KN30/KVAR |  |  |  | CDC | 299 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳30線 | 佳30線 |  | 佳30線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳30線A1 | 11KV佳30線 R相AMP | FEEDER | S76/11/KN30/I_R |  |  |  | CDC | 300 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳30線 | 佳30線 |  | 佳30線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳30線A2 | 11KV佳30線 S相AMP | FEEDER | S76/11/KN30/I_S |  |  |  | CDC | 301 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳30線 | 佳30線 |  | 佳30線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳30線A3 | 11KV佳30線 T相AMP | FEEDER | S76/11/KN30/I_T |  |  |  | CDC | 302 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳30線 | 佳30線 |  | 佳30線A0 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳30線A0 | 11KV佳30線 N相AMP | FEEDER | S76/11/KN30/I_N |  |  |  | CDC | 303 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳45線 | 佳45線 |  | 佳45線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳45線KVAR | 11KV佳45線 KVAR | FEEDER | S76/11/KN45/KVAR |  |  |  | CDC | 304 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳45線 | 佳45線 |  | 佳45線A1 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳45線A1 | 11KV佳45線 R相AMP | FEEDER | S76/11/KN45/I_R |  |  |  | CDC | 305 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳45線 | 佳45線 |  | 佳45線A2 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳45線A2 | 11KV佳45線 S相AMP | FEEDER | S76/11/KN45/I_S |  |  |  | CDC | 306 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳45線 | 佳45線 |  | 佳45線A3 | [17 empty] | 2-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳45線A3 | 11KV佳45線 T相AMP | FEEDER | S76/11/KN45/I_T |  |  |  | CDC | 307 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 佳45線 | 佳45線 |  | 佳45線A0 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.佳45線A0 | 11KV佳45線 N相AMP | FEEDER | S76/11/KN45/I_N |  |  |  | CDC | 308 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.730_MW | 學甲佳里一路 MW | LINE69 | S76/69/730/MW |  |  |  | CDC | 309 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.730_MVAR | 學甲佳里一路 MVAR | LINE69 | S76/69/730/MVAR |  |  |  | CDC | 310 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備01線 | 備01線 |  | 備01線KVAR | [17 empty] | 2-CE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備01線KVAR | 11KV備01線 KVAR | FEEDER | S76/11/KN01/KVAR |  |  |  | CDC | 311 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備01線 | 備01線 |  | 備01線A1 | [17 empty] | 2-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備01線A1 | 11KV備01線 R相AMP | FEEDER | S76/11/KN01/I_R |  |  |  | CDC | 312 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備01線 | 備01線 |  | 備01線A2 | [17 empty] | 2-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備01線A2 | 11KV備01線 S相AMP | FEEDER | S76/11/KN01/I_S |  |  |  | CDC | 313 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備01線 | 備01線 |  | 備01線A3 | [17 empty] | 2-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備01線A3 | 11KV備01線 T相AMP | FEEDER | S76/11/KN01/I_T |  |  |  | CDC | 314 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備01線 | 備01線 |  | 備01線A0 | [17 empty] | 2-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備01線A0 | 11KV備01線 N相AMP | FEEDER | S76/11/KN01/I_N |  |  |  | CDC | 315 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-8D | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | S76/69/2BUS/V |  |  |  | CDC | 316 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S76 | 佳里一SS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-8E | [5 empty] | A_-1200_1200(-2000_2000) |  | ADCS_N | [8 empty] | 佳一SS.600TIE_AMP | 600TIE AMP | TIE | S76/69/600/I |  |  |  | CDC | 317 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | C12R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1200.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | S76/11/2ABUS/V_R |  |  |  | CDC | 318 | GENERICAIPoint | SS417_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-DB | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | S76/11/2BBUS/V_R |  |  |  | CDC | 319 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S76 | 佳里一SS | 11 | 11kV | 備02線 | 備02線 |  | 備02線KVAR | [17 empty] | 2-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備02線KVAR | 11KV備02線 KVAR | FEEDER | S76/11/KN02/KVAR |  |  |  | CDC | 320 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備02線 | 備02線 |  | 備02線A1 | [17 empty] | 2-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備02線A1 | 11KV備02線 R相AMP | FEEDER | S76/11/KN02/I_R |  |  |  | CDC | 321 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備02線 | 備02線 |  | 備02線A2 | [17 empty] | 2-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備02線A2 | 11KV備02線 S相AMP | FEEDER | S76/11/KN02/I_S |  |  |  | CDC | 322 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備02線 | 備02線 |  | 備02線A3 | [17 empty] | 2-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備02線A3 | 11KV備02線 T相AMP | FEEDER | S76/11/KN02/I_T |  |  |  | CDC | 323 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 11 | 11kV | 備02線 | 備02線 |  | 備02線A0 | [17 empty] | 2-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳一SS.備02線A0 | 11KV備02線 N相AMP | FEEDER | S76/11/KN02/I_N |  |  |  | CDC | 324 | GENERICAIPoint | SS417_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | PHA | [17 empty] | 1-10-02 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.620_PHA | 學甲佳里二路(620) 相間RY | LINE69 | S76/69/620/PHA |  |  |  | CDC | 325 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.620_GDA | 學甲佳里二路(620) 接地RY | LINE69 | S76/69/620/GDA |  |  |  | CDC | 326 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲線(620) |  | 74A | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.620_74A | 學甲線(620) 74RY | LINE69 |  |  |  |  | CDC | 327 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | CB | [17 empty] | 1-10-00 |  | 1-01 | [5 empty] | 69KV_N | [8 empty] | 佳一SS.620_CB | 620(學甲佳里二路) CB | LINE69 | S76/69/620/CB |  |  |  | CDC | 328 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | PHA | [17 empty] | 1-15-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_PHA | 11KV漚汪線(KN21) 相間RY | FEEDER | S76/11/KN21/PHA |  |  |  | CDC | 329 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) |  | GDA | [17 empty] | 1-15-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_GDA | 11KV漚汪線(KN21) 接地RY | FEEDER | S76/11/KN21/GDA |  |  |  | CDC | 330 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_79UL | 11KV漚汪線(KN21) 79RY U/L | FEEDER | S76/11/KN21/79UL |  |  |  | CDC | 331 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN21 | 漚汪線(KN21) LCO分流器 |  | ADJ | [17 empty] | 2-34-00 |  | 2-18 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_ADJ | 11KV漚汪線(KN21) LCO分流器 U/L | FEEDER | S76/11/KN21/ADJ |  |  |  | CDC | 332 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN21 | KN21(11KV漚汪線) |  | CB | [17 empty] | 1-14-00 |  | 1-34 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_CB | KN21(11KV漚汪線) CB | FEEDER | S76/11/KN21/CB |  |  |  | CDC | 333 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | PHA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_PHA | 11KV佳興線(KN22) 相間RY | FEEDER | S76/11/KN22/PHA |  |  |  | CDC | 334 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) |  | GDA | [17 empty] | 1-15-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_GDA | 11KV佳興線(KN22) 接地RY | FEEDER | S76/11/KN22/GDA |  |  |  | CDC | 335 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_79UL | 11KV佳興線(KN22) 79RY U/L | FEEDER | S76/11/KN22/79UL |  |  |  | CDC | 336 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN22 | 佳興線(KN22) LCO分流器 |  | ADJ | [17 empty] | 2-34-01 |  | 2-19 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_ADJ | 11KV佳興線(KN22) LCO分流器 U/L | FEEDER | S76/11/KN22/ADJ |  |  |  | CDC | 337 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN22 | KN22(11KV佳興線) |  | CB | [17 empty] | 1-14-01 |  | 1-35 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_CB | KN22(11KV佳興線) CB | FEEDER | S76/11/KN22/CB |  |  |  | CDC | 338 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_PHA | 11KV佳工線(KN23) 相間RY | FEEDER | S76/11/KN23/PHA |  |  |  | CDC | 339 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_GDA | 11KV佳工線(KN23) 接地RY | FEEDER | S76/11/KN23/GDA |  |  |  | CDC | 340 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_79UL | 11KV佳工線(KN23) 79RY U/L | FEEDER | S76/11/KN23/79UL |  |  |  | CDC | 341 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN23 | 佳工線(KN23) LCO分流器 |  | ADJ | [17 empty] | 2-34-02 |  | 2-1A | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_ADJ | 11KV佳工線(KN23) LCO分流器 U/L | FEEDER | S76/11/KN23/ADJ |  |  |  | CDC | 342 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN23 | KN23(11KV佳工線) |  | CB | [17 empty] | 1-14-02 |  | 1-36 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_CB | KN23(11KV佳工線) CB | FEEDER | S76/11/KN23/CB |  |  |  | CDC | 343 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | PHA | [17 empty] | 1-15-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_PHA | 11KV通吉線(KN24) 相間RY | FEEDER | S76/11/KN24/PHA |  |  |  | CDC | 344 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) |  | GDA | [17 empty] | 1-16-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_GDA | 11KV通吉線(KN24) 接地RY | FEEDER | S76/11/KN24/GDA |  |  |  | CDC | 345 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_79UL | 11KV通吉線(KN24) 79RY U/L | FEEDER | S76/11/KN24/79UL |  |  |  | CDC | 346 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN24 | 通吉線(KN24) LCO分流器 |  | ADJ | [17 empty] | 2-34-03 |  | 2-1B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_ADJ | 11KV通吉線(KN24) LCO分流器 U/L | FEEDER | S76/11/KN24/ADJ |  |  |  | CDC | 347 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN24 | KN24(11KV通吉線) |  | CB | [17 empty] | 1-14-03 |  | 1-37 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_CB | KN24(11KV通吉線) CB | FEEDER | S76/11/KN24/CB |  |  |  | CDC | 348 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | PHA | [17 empty] | 1-16-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_PHA | 11KV佳25線(KN25) 相間RY | FEEDER | S76/11/KN25/PHA |  |  |  | CDC | 349 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) |  | GDA | [17 empty] | 1-16-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_GDA | 11KV佳25線(KN25) 接地RY | FEEDER | S76/11/KN25/GDA |  |  |  | CDC | 350 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_79UL | 11KV佳25線(KN25) 79RY U/L | FEEDER | S76/11/KN25/79UL |  |  |  | CDC | 351 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN25 | 佳25線(KN25) LCO分流器 |  | ADJ | [17 empty] | 2-34-04 |  | 2-1C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_ADJ | 11KV佳25線(KN25) LCO分流器 U/L | FEEDER | S76/11/KN25/ADJ |  |  |  | CDC | 352 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN25 | KN25(11KV佳25線) |  | CB | [17 empty] | 1-14-04 |  | 1-38 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_CB | KN25(11KV佳25線) CB | FEEDER | S76/11/KN25/CB |  |  |  | CDC | 353 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_PHA | 11KV漳洲線(KN26) 相間RY | FEEDER | S76/11/KN26/PHA |  |  |  | CDC | 354 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_GDA | 11KV漳洲線(KN26) 接地RY | FEEDER | S76/11/KN26/GDA |  |  |  | CDC | 355 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) 79RY |  | 79UL | [17 empty] | 2-30-07 |  | 1-51 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_79UL | 11KV漳洲線(KN26) 79RY U/L | FEEDER | S76/11/KN26/79UL |  |  |  | CDC | 356 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN26 | 漳洲線(KN26) LCO分流器 |  | ADJ | [17 empty] | 2-34-05 |  | 2-1D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_ADJ | 11KV漳洲線(KN26) LCO分流器 U/L | FEEDER | S76/11/KN26/ADJ |  |  |  | CDC | 357 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN26 | KN26(11KV漳洲線) |  | CB | [17 empty] | 1-16-06 |  | 1-49 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_CB | KN26(11KV漳洲線) CB | FEEDER | S76/11/KN26/CB |  |  |  | CDC | 358 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | PHA | [17 empty] | 1-18-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_PHA | 11KV頂城線(KN27) 相間RY | FEEDER | S76/11/KN27/PHA |  |  |  | CDC | 359 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) |  | GDA | [17 empty] | 1-18-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_GDA | 11KV頂城線(KN27) 接地RY | FEEDER | S76/11/KN27/GDA |  |  |  | CDC | 360 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 1-52 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_79UL | 11KV頂城線(KN27) 79RY U/L | FEEDER | S76/11/KN27/79UL |  |  |  | CDC | 361 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN27 | 頂城線(KN27) LCO分流器 |  | ADJ | [17 empty] | 2-34-06 |  | 2-1E | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_ADJ | 11KV頂城線(KN27) LCO分流器 U/L | FEEDER | S76/11/KN27/ADJ |  |  |  | CDC | 362 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN27 | KN27(11KV頂城線) |  | CB | [17 empty] | 1-16-07 |  | 1-4A | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_CB | KN27(11KV頂城線) CB | FEEDER | S76/11/KN27/CB |  |  |  | CDC | 363 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | PHA | [17 empty] | 1-18-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_PHA | 11KV七股線(KN28) 相間RY | FEEDER | S76/11/KN28/PHA |  |  |  | CDC | 364 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) |  | GDA | [17 empty] | 1-18-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_GDA | 11KV七股線(KN28) 接地RY | FEEDER | S76/11/KN28/GDA |  |  |  | CDC | 365 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) 79RY |  | 79UL | [17 empty] | 2-30-09 |  | 1-53 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_79UL | 11KV七股線(KN28) 79RY U/L | FEEDER | S76/11/KN28/79UL |  |  |  | CDC | 366 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN28 | 七股線(KN28) LCO分流器 |  | ADJ | [17 empty] | 2-34-07 |  | 2-1F | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_ADJ | 11KV七股線(KN28) LCO分流器 U/L | FEEDER | S76/11/KN28/ADJ |  |  |  | CDC | 367 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN28 | KN28(11KV七股線) |  | CB | [17 empty] | 1-17-00 |  | 1-4B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_CB | KN28(11KV七股線) CB | FEEDER | S76/11/KN28/CB |  |  |  | CDC | 368 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_PHA | 11KV塭寮線(KN29) 相間RY | FEEDER | S76/11/KN29/PHA |  |  |  | CDC | 369 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_GDA | 11KV塭寮線(KN29) 接地RY | FEEDER | S76/11/KN29/GDA |  |  |  | CDC | 370 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 1-54 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_79UL | 11KV塭寮線(KN29) 79RY U/L | FEEDER | S76/11/KN29/79UL |  |  |  | CDC | 371 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN29 | 塭寮線(KN29) LCO分流器 |  | ADJ | [17 empty] | 2-34-08 |  | 2-20 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_ADJ | 11KV塭寮線(KN29) LCO分流器 U/L | FEEDER | S76/11/KN29/ADJ |  |  |  | CDC | 372 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN29 | KN29(11KV塭寮線) |  | CB | [17 empty] | 1-17-01 |  | 1-4C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_CB | KN29(11KV塭寮線) CB | FEEDER | S76/11/KN29/CB |  |  |  | CDC | 373 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | PHA | [17 empty] | 1-18-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_PHA | 11KV佳30線(KN30) 相間RY | FEEDER | S76/11/KN30/PHA |  |  |  | CDC | 374 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) |  | GDA | [17 empty] | 1-19-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_GDA | 11KV佳30線(KN30) 接地RY | FEEDER | S76/11/KN30/GDA |  |  |  | CDC | 375 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 1-55 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_79UL | 11KV佳30線(KN30) 79RY U/L | FEEDER | S76/11/KN30/79UL |  |  |  | CDC | 376 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN30 | 佳30線(KN30) LCO分流器 |  | ADJ | [17 empty] | 2-34-09 |  | 2-21 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_ADJ | 11KV佳30線(KN30) LCO分流器 U/L | FEEDER | S76/11/KN30/ADJ |  |  |  | CDC | 377 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN30 | KN30(11KV佳30線) |  | CB | [17 empty] | 1-17-02 |  | 1-4D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_CB | KN30(11KV佳30線) CB | FEEDER | S76/11/KN30/CB |  |  |  | CDC | 378 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | PHA | [17 empty] | 1-1A-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_PHA | 11KV西港線(KN31) 相間RY | FEEDER | S76/11/KN31/PHA |  |  |  | CDC | 379 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) |  | GDA | [17 empty] | 1-1A-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_GDA | 11KV西港線(KN31) 接地RY | FEEDER | S76/11/KN31/GDA |  |  |  | CDC | 380 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) 79RY |  | 79UL | [17 empty] | 2-31-07 |  | 1-65 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_79UL | 11KV西港線(KN31) 79RY U/L | FEEDER | S76/11/KN31/79UL |  |  |  | CDC | 381 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN31 | 西港線(KN31) LCO分流器 |  | ADJ | [17 empty] | 2-34-10 |  | 2-22 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_ADJ | 11KV西港線(KN31) LCO分流器 U/L | FEEDER | S76/11/KN31/ADJ |  |  |  | CDC | 382 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN31 | KN31(11KV西港線) |  | CB | [17 empty] | 1-19-04 |  | 1-5D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_CB | KN31(11KV西港線) CB | FEEDER | S76/11/KN31/CB |  |  |  | CDC | 383 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | PHA | [17 empty] | 1-1A-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_PHA | 11KV子良線(KN32) 相間RY | FEEDER | S76/11/KN32/PHA |  |  |  | CDC | 384 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) |  | GDA | [17 empty] | 1-1B-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_GDA | 11KV子良線(KN32) 接地RY | FEEDER | S76/11/KN32/GDA |  |  |  | CDC | 385 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 1-66 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_79UL | 11KV子良線(KN32) 79RY U/L | FEEDER | S76/11/KN32/79UL |  |  |  | CDC | 386 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN32 | 子良線(KN32) LCO分流器 |  | ADJ | [17 empty] | 2-34-11 |  | 2-23 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_ADJ | 11KV子良線(KN32) LCO分流器 U/L | FEEDER | S76/11/KN32/ADJ |  |  |  | CDC | 387 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN32 | KN32(11KV子良線) |  | CB | [17 empty] | 1-19-05 |  | 1-5E | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_CB | KN32(11KV子良線) CB | FEEDER | S76/11/KN32/CB |  |  |  | CDC | 388 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | PHA | [17 empty] | 1-1B-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_PHA | 11KV嘉福線(KN33) 相間RY | FEEDER | S76/11/KN33/PHA |  |  |  | CDC | 389 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) |  | GDA | [17 empty] | 1-1B-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_GDA | 11KV嘉福線(KN33) 接地RY | FEEDER | S76/11/KN33/GDA |  |  |  | CDC | 390 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 1-67 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_79UL | 11KV嘉福線(KN33) 79RY U/L | FEEDER | S76/11/KN33/79UL |  |  |  | CDC | 391 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN33 | 嘉福線(KN33) LCO分流器 |  | ADJ | [17 empty] | 2-34-12 |  | 2-24 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_ADJ | 11KV嘉福線(KN33) LCO分流器 U/L | FEEDER | S76/11/KN33/ADJ |  |  |  | CDC | 392 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN33 | KN33(11KV嘉福線) |  | CB | [17 empty] | 1-19-06 |  | 1-5F | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_CB | KN33(11KV嘉福線) CB | FEEDER | S76/11/KN33/CB |  |  |  | CDC | 393 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | PHA | [17 empty] | 1-1B-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_PHA | 11KV篤加線(KN34) 相間RY | FEEDER | S76/11/KN34/PHA |  |  |  | CDC | 394 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) |  | GDA | [17 empty] | 1-1B-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_GDA | 11KV篤加線(KN34) 接地RY | FEEDER | S76/11/KN34/GDA |  |  |  | CDC | 395 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 1-68 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_79UL | 11KV篤加線(KN34) 79RY U/L | FEEDER | S76/11/KN34/79UL |  |  |  | CDC | 396 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN34 | 篤加線(KN34) LCO分流器 |  | ADJ | [17 empty] | 2-34-13 |  | 2-25 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_ADJ | 11KV篤加線(KN34) LCO分流器 U/L | FEEDER | S76/11/KN34/ADJ |  |  |  | CDC | 397 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN34 | KN34(11KV篤加線) |  | CB | [17 empty] | 1-19-07 |  | 1-60 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_CB | KN34(11KV篤加線) CB | FEEDER | S76/11/KN34/CB |  |  |  | CDC | 398 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | PHA | [17 empty] | 1-1B-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_PHA | 11KV林樂線(KN35) 相間RY | FEEDER | S76/11/KN35/PHA |  |  |  | CDC | 399 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) |  | GDA | [17 empty] | 1-1B-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_GDA | 11KV林樂線(KN35) 接地RY | FEEDER | S76/11/KN35/GDA |  |  |  | CDC | 400 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) 79RY |  | 79UL | [17 empty] | 2-31-11 |  | 1-69 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_79UL | 11KV林樂線(KN35) 79RY U/L | FEEDER | S76/11/KN35/79UL |  |  |  | CDC | 401 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN35 | 林樂線(KN35) LCO分流器 |  | ADJ | [17 empty] | 2-34-14 |  | 2-26 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_ADJ | 11KV林樂線(KN35) LCO分流器 U/L | FEEDER | S76/11/KN35/ADJ |  |  |  | CDC | 402 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN35 | KN35(11KV林樂線) |  | CB | [17 empty] | 1-1A-00 |  | 1-61 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_CB | KN35(11KV林樂線) CB | FEEDER | S76/11/KN35/CB |  |  |  | CDC | 403 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | PHA | [17 empty] | 1-1D-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_PHA | 11KV三股線(KN36) 相間RY | FEEDER | S76/11/KN36/PHA |  |  |  | CDC | 404 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) |  | GDA | [17 empty] | 1-1D-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_GDA | 11KV三股線(KN36) 接地RY | FEEDER | S76/11/KN36/GDA |  |  |  | CDC | 405 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) 79RY |  | 79UL | [17 empty] | 2-32-07 |  | 1-79 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_79UL | 11KV三股線(KN36) 79RY U/L | FEEDER | S76/11/KN36/79UL |  |  |  | CDC | 406 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN36 | 三股線(KN36) LCO分流器 |  | ADJ | [17 empty] | 2-34-15 |  | 2-27 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_ADJ | 11KV三股線(KN36) LCO分流器 U/L | FEEDER | S76/11/KN36/ADJ |  |  |  | CDC | 407 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN36 | KN36(11KV三股線) |  | CB | [17 empty] | 1-1C-03 |  | 1-71 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_CB | KN36(11KV三股線) CB | FEEDER | S76/11/KN36/CB |  |  |  | CDC | 408 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | PHA | [17 empty] | 1-1D-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_PHA | 11KV佳塭線(KN37) 相間RY | FEEDER | S76/11/KN37/PHA |  |  |  | CDC | 409 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) |  | GDA | [17 empty] | 1-1D-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_GDA | 11KV佳塭線(KN37) 接地RY | FEEDER | S76/11/KN37/GDA |  |  |  | CDC | 410 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) 79RY |  | 79UL | [17 empty] | 2-32-08 |  | 1-7A | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_79UL | 11KV佳塭線(KN37) 79RY U/L | FEEDER | S76/11/KN37/79UL |  |  |  | CDC | 411 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN37 | 佳塭線(KN37) LCO分流器 |  | ADJ | [17 empty] | 2-35-00 |  | 2-28 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_ADJ | 11KV佳塭線(KN37) LCO分流器 U/L | FEEDER | S76/11/KN37/ADJ |  |  |  | CDC | 412 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN37 | KN37(11KV佳塭線) |  | CB | [17 empty] | 1-1C-04 |  | 1-72 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_CB | KN37(11KV佳塭線) CB | FEEDER | S76/11/KN37/CB |  |  |  | CDC | 413 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | PHA | [17 empty] | 1-1E-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_PHA | 11KV光復線(KN38) 相間RY | FEEDER | S76/11/KN38/PHA |  |  |  | CDC | 414 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) |  | GDA | [17 empty] | 1-1E-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_GDA | 11KV光復線(KN38) 接地RY | FEEDER | S76/11/KN38/GDA |  |  |  | CDC | 415 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) 79RY |  | 79UL | [17 empty] | 2-32-09 |  | 1-7B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_79UL | 11KV光復線(KN38) 79RY U/L | FEEDER | S76/11/KN38/79UL |  |  |  | CDC | 416 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN38 | 光復線(KN38) LCO分流器 |  | ADJ | [17 empty] | 2-35-01 |  | 2-29 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_ADJ | 11KV光復線(KN38) LCO分流器 U/L | FEEDER | S76/11/KN38/ADJ |  |  |  | CDC | 417 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN38 | KN38(11KV光復線) |  | CB | [17 empty] | 1-1C-05 |  | 1-73 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_CB | KN38(11KV光復線) CB | FEEDER | S76/11/KN38/CB |  |  |  | CDC | 418 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | PHA | [17 empty] | 1-1E-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_PHA | 11KV新生線(KN39) 相間RY | FEEDER | S76/11/KN39/PHA |  |  |  | CDC | 419 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) |  | GDA | [17 empty] | 1-1E-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_GDA | 11KV新生線(KN39) 接地RY | FEEDER | S76/11/KN39/GDA |  |  |  | CDC | 420 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) 79RY |  | 79UL | [17 empty] | 2-32-10 |  | 1-7C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_79UL | 11KV新生線(KN39) 79RY U/L | FEEDER | S76/11/KN39/79UL |  |  |  | CDC | 421 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN39 | 新生線(KN39) LCO分流器 |  | ADJ | [17 empty] | 2-35-02 |  | 2-2A | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_ADJ | 11KV新生線(KN39) LCO分流器 U/L | FEEDER | S76/11/KN39/ADJ |  |  |  | CDC | 422 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN39 | KN39(11KV新生線) |  | CB | [17 empty] | 1-1C-06 |  | 1-74 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_CB | KN39(11KV新生線) CB | FEEDER | S76/11/KN39/CB |  |  |  | CDC | 423 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | PHA | [17 empty] | 1-1E-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_PHA | 11KV仁愛線(KN40) 相間RY | FEEDER | S76/11/KN40/PHA |  |  |  | CDC | 424 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) |  | GDA | [17 empty] | 1-1E-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_GDA | 11KV仁愛線(KN40) 接地RY | FEEDER | S76/11/KN40/GDA |  |  |  | CDC | 425 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) 79RY |  | 79UL | [17 empty] | 2-32-11 |  | 1-7D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_79UL | 11KV仁愛線(KN40) 79RY U/L | FEEDER | S76/11/KN40/79UL |  |  |  | CDC | 426 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN40 | 仁愛線(KN40) LCO分流器 |  | ADJ | [17 empty] | 2-35-03 |  | 2-2B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_ADJ | 11KV仁愛線(KN40) LCO分流器 U/L | FEEDER | S76/11/KN40/ADJ |  |  |  | CDC | 427 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN40 | KN40(11KV仁愛線) |  | CB | [17 empty] | 1-1C-07 |  | 1-75 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_CB | KN40(11KV仁愛線) CB | FEEDER | S76/11/KN40/CB |  |  |  | CDC | 428 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | PHA | [17 empty] | 2-10-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_PHA | 11KV北農線(KN41) 相間RY | FEEDER | S76/11/KN41/PHA |  |  |  | CDC | 429 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) |  | GDA | [17 empty] | 2-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_GDA | 11KV北農線(KN41) 接地RY | FEEDER | S76/11/KN41/GDA |  |  |  | CDC | 430 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) 79RY |  | 79UL | [17 empty] | 2-33-08 |  | 2-0D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_79UL | 11KV北農線(KN41) 79RY U/L | FEEDER | S76/11/KN41/79UL |  |  |  | CDC | 431 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN41 | 北農線(KN41) LCO分流器 |  | ADJ | [17 empty] | 2-35-05 |  | 2-2D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_ADJ | 11KV北農線(KN41) LCO分流器 U/L | FEEDER | S76/11/KN41/ADJ |  |  |  | CDC | 432 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN41 | KN41(11KV北農線) |  | CB | [17 empty] | 1-1F-02 |  | 2-05 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_CB | KN41(11KV北農線) CB | FEEDER | S76/11/KN41/CB |  |  |  | CDC | 433 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | PHA | [17 empty] | 2-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_PHA | 11KV中山線(KN42) 相間RY | FEEDER | S76/11/KN42/PHA |  |  |  | CDC | 434 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) |  | GDA | [17 empty] | 2-10-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_GDA | 11KV中山線(KN42) 接地RY | FEEDER | S76/11/KN42/GDA |  |  |  | CDC | 435 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) 79RY |  | 79UL | [17 empty] | 2-33-09 |  | 2-0E | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_79UL | 11KV中山線(KN42) 79RY U/L | FEEDER | S76/11/KN42/79UL |  |  |  | CDC | 436 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN42 | 中山線(KN42) LCO分流器 |  | ADJ | [17 empty] | 2-35-06 |  | 2-2E | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_ADJ | 11KV中山線(KN42) LCO分流器 U/L | FEEDER | S76/11/KN42/ADJ |  |  |  | CDC | 437 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN42 | KN42(11KV中山線) |  | CB | [17 empty] | 1-1F-03 |  | 2-06 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_CB | KN42(11KV中山線) CB | FEEDER | S76/11/KN42/CB |  |  |  | CDC | 438 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | PHA | [17 empty] | 2-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_PHA | 11KV佳麻線(KN43) 相間RY | FEEDER | S76/11/KN43/PHA |  |  |  | CDC | 439 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) |  | GDA | [17 empty] | 2-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_GDA | 11KV佳麻線(KN43) 接地RY | FEEDER | S76/11/KN43/GDA |  |  |  | CDC | 440 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) 79RY |  | 79UL | [17 empty] | 2-33-10 |  | 2-0F | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_79UL | 11KV佳麻線(KN43) 79RY U/L | FEEDER | S76/11/KN43/79UL |  |  |  | CDC | 441 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN43 | 佳麻線(KN43) LCO分流器 |  | ADJ | [17 empty] | 2-35-07 |  | 2-2F | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_ADJ | 11KV佳麻線(KN43) LCO分流器 U/L | FEEDER | S76/11/KN43/ADJ |  |  |  | CDC | 442 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN43 | KN43(11KV佳麻線) |  | CB | [17 empty] | 1-1F-04 |  | 2-07 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_CB | KN43(11KV佳麻線) CB | FEEDER | S76/11/KN43/CB |  |  |  | CDC | 443 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | PHA | [17 empty] | 2-11-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_PHA | 11KV佳西線(KN44) 相間RY | FEEDER | S76/11/KN44/PHA |  |  |  | CDC | 444 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) |  | GDA | [17 empty] | 2-11-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_GDA | 11KV佳西線(KN44) 接地RY | FEEDER | S76/11/KN44/GDA |  |  |  | CDC | 445 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) 79RY |  | 79UL | [17 empty] | 2-33-11 |  | 2-10 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_79UL | 11KV佳西線(KN44) 79RY U/L | FEEDER | S76/11/KN44/79UL |  |  |  | CDC | 446 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN44 | 佳西線(KN44) LCO分流器 |  | ADJ | [17 empty] | 2-35-08 |  | 2-30 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_ADJ | 11KV佳西線(KN44) LCO分流器 U/L | FEEDER | S76/11/KN44/ADJ |  |  |  | CDC | 447 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN44 | KN44(11KV佳西線) |  | CB | [17 empty] | 1-1F-05 |  | 2-08 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_CB | KN44(11KV佳西線) CB | FEEDER | S76/11/KN44/CB |  |  |  | CDC | 448 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | PHA | [17 empty] | 2-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_PHA | 11KV佳45線(KN45) 相間RY | FEEDER | S76/11/KN45/PHA |  |  |  | CDC | 449 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) |  | GDA | [17 empty] | 2-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_GDA | 11KV佳45線(KN45) 接地RY | FEEDER | S76/11/KN45/GDA |  |  |  | CDC | 450 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) 79RY |  | 79UL | [17 empty] | 2-33-07 |  | 2-0C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_79UL | 11KV佳45線(KN45) 79RY U/L | FEEDER | S76/11/KN45/79UL |  |  |  | CDC | 451 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN45 | 佳45線(KN45) LCO分流器 |  | ADJ | [17 empty] | 2-35-04 |  | 2-2C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_ADJ | 11KV佳45線(KN45) LCO分流器 U/L | FEEDER | S76/11/KN45/ADJ |  |  |  | CDC | 452 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN45 | KN45(11KV佳45線) |  | CB | [17 empty] | 1-1F-01 |  | 2-04 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_CB | KN45(11KV佳45線) CB | FEEDER | S76/11/KN45/CB |  |  |  | CDC | 453 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | TIE1 | #2B-#1 |  | CB | [17 empty] | 1-14-05 |  | 1-32 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE1_CB | 11KV #2B-#1 TIE CB | TIE | S76/11/TIE1/CB |  |  |  | CDC | 454 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE1 | #2B-#1 |  | 51A | [17 empty] | 1-16-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE1_51A | 11KV #2B-#1 TIE 51RY | TIE | S76/11/TIE1/51A |  |  |  | CDC | 455 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE1 | #2B-#1 |  | 51NA | [17 empty] | 1-16-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE1_51NA | 11KV #2B-#1 TIE 51N RY | TIE | S76/11/TIE1/51NA |  |  |  | CDC | 456 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE2 | #3-#2A |  | CB | [17 empty] | 1-17-03 |  | 1-47 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE2_CB | 11KV #3-#2A TIE CB | TIE | S76/11/TIE2/CB |  |  |  | CDC | 457 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE2 | #3-#2A |  | 51A | [17 empty] | 1-19-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE2_51A | 11KV #3-#2A TIE 51RY | TIE | S76/11/TIE2/51A |  |  |  | CDC | 458 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE2 | #3-#2A |  | 51NA | [17 empty] | 1-19-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE2_51NA | 11KV #3-#2A TIE 51N RY | TIE | S76/11/TIE2/51NA |  |  |  | CDC | 459 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE3 |  | CB | [17 empty] | 1-1A-01 |  | 1-5B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE3_CB | 11KV TIE3 CB | TIE | S76/11/TIE3/CB |  |  |  | CDC | 460 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE3 |  | 51A | [17 empty] | 1-1C-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE3_51A | 11KV TIE3 51RY | TIE | S76/11/TIE3/51A |  |  |  | CDC | 461 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE3 | TIE3 |  | 51NA | [17 empty] | 1-1C-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE3_51NA | 11KV TIE3 51N RY | TIE | S76/11/TIE3/51NA |  |  |  | CDC | 462 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE4 | #4-#5 |  | CB | [17 empty] | 1-1D-00 |  | 1-6F | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE4_CB | 11KV #4-#5 TIE CB | TIE | S76/11/TIE4/CB |  |  |  | CDC | 463 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE4 | #4-#5 |  | 51A | [17 empty] | 1-1E-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE4_51A | 11KV #4-#5 TIE 51RY | TIE | S76/11/TIE4/51A |  |  |  | CDC | 464 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE4 | #4-#5 |  | 51NA | [17 empty] | 1-1E-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE4_51NA | 11KV #4-#5 TIE 51N RY | TIE | S76/11/TIE4/51NA |  |  |  | CDC | 465 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE5 |  | CB | [17 empty] | 2-11-03 |  | 2-12 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE5_CB | 11KV TIE5 CB | TIE | S76/11/TIE5/CB |  |  |  | CDC | 466 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE5 |  | 51A | [17 empty] | 2-11-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE5_51A | 11KV TIE5 51RY | TIE | S76/11/TIE5/51A |  |  |  | CDC | 467 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | TIE5 | TIE5 |  | 51NA | [17 empty] | 2-11-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE5_51NA | 11KV TIE5 51N RY | TIE | S76/11/TIE5/51NA |  |  |  | CDC | 468 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.750_CB | 750(#1MTR) CB | DTR | S76/69/750/CB |  |  |  | CDC | 469 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 1M | #1MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.1M_CB | 1M(#1MTR) CB | DTR | S76/11/M1/CB |  |  |  | CDC | 470 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_51A | #1MTR 51RY | DTR | S76/69/750/51A |  |  |  | CDC | 471 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_51NA | #1MTR 51N RY | DTR | S76/69/750/51NA |  |  |  | CDC | 472 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_51ZA | #1MTR 51Z RY | DTR | S76//1MTR/51ZA |  |  |  | CDC | 473 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_87A | #1MTR 87RY | DTR | S76//1MTR/87A |  |  |  | CDC | 474 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_87UL | #1MTR 87RY U/L | DTR | S76//1MTR/87UL |  |  |  | CDC | 475 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | 1M | #1MTR二次側(1M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.1M_51A | #1MTR二次側(1M) 51RY | DTR | S76/11/M1/51A |  |  |  | CDC | 476 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_TRA | #1MTR 重故障 | DTR | S76//1MTR/TRA |  |  |  | CDC | 477 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_TRF | #1MTR 輕故障 | DTR | S76//1MTR/TRF |  |  |  | CDC | 478 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_S/L | #1MTR OLTC S/L | DTR | S76//1MTR/SupLocal |  |  |  | CDC | 479 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_A/M | #1MTR OLTC A/M | DTR | S76//1MTR/Tap Chan |  |  |  | CDC | 480 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_OLTC遲滯 | #1MTR OLTC遲滯 | DTR | S76//1MTR/OLTC_DLY |  |  |  | CDC | 481 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR_AC | #1MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_AC_FAULT | #1MTR AC電源失效 | DTR | S76//1MTR/AC_Fault |  |  |  | CDC | 482 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.760_CB | 760(#2MTR) CB | DTR | S76/69/760/CB |  |  |  | CDC | 483 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_51A | #2MTR 51RY | DTR | S76/69/760/51A |  |  |  | CDC | 484 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_51NA | #2MTR 51N RY | DTR | S76/69/760/51NA |  |  |  | CDC | 485 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_51ZA | #2MTR 51Z RY | DTR | S76//2MTR/51ZA |  |  |  | CDC | 486 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_87A | #2MTR 87RY | DTR | S76//2MTR/87A |  |  |  | CDC | 487 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 87UL | [17 empty] | 2-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_87UL | #2MTR 87RY U/L | DTR | S76//2MTR/87UL |  |  |  | CDC | 488 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | 2MTR | #760 |  | 81AS | [17 empty] | 1-14-06 |  | 1-41 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_81A/S | #760 #780 81RY A/S | DTR | S76/69/760/81AS |  |  |  | CDC | 489 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 2-30-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_TRA | #2MTR 重故障 | DTR | S76//2MTR/TRA |  |  |  | CDC | 490 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 2-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_TRF | #2MTR 輕故障 | DTR | S76//2MTR/TRF |  |  |  | CDC | 491 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 2-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_S/L | #2MTR OLTC S/L | DTR | S76//2MTR/SupLocal |  |  |  | CDC | 492 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 2-30-05 |  | 1-4F | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_A/M | #2MTR OLTC A/M | DTR | S76//2MTR/Tap Chan |  |  |  | CDC | 493 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | OLTC_DLY | [17 empty] | 2-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_OLTC遲滯 | #2MTR OLTC遲滯 | DTR | S76//2MTR/OLTC_DLY |  |  |  | CDC | 494 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR_AC | #2MTR |  | FAULT | [17 empty] | 2-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_AC_FAULT | #2MTR AC電源失效 | DTR | S76//2MTR/AC_Fault |  |  |  | CDC | 495 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-02-06 |  | 1-58 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.770_CB | 770(#3MTR) CB | DTR | S76/69/770/CB |  |  |  | CDC | 496 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 3M | #3MTR |  | CB | [17 empty] | 1-02-07 |  | 1-59 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.3M_CB | 3M(#3MTR) CB | DTR | S76/11/M3/CB |  |  |  | CDC | 497 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 51A | [17 empty] | 1-03-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_51A | #3MTR 51RY | DTR | S76/69/770/51A |  |  |  | CDC | 498 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 51NA | [17 empty] | 1-03-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_51NA | #3MTR 51N RY | DTR | S76/69/770/51NA |  |  |  | CDC | 499 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-04-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_51ZA | #3MTR 51Z RY | DTR | S76//3MTR/51ZA |  |  |  | CDC | 500 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-03-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_87A | #3MTR 87RY | DTR | S76//3MTR/87A |  |  |  | CDC | 501 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 87UL | [17 empty] | 2-31-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_87UL | #3MTR 87RY U/L | DTR | S76//3MTR/87UL |  |  |  | CDC | 502 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | 3MTR | #770 |  | 81AS | [17 empty] | 1-1A-02 |  | 1-6A | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_81A/S | #770 81RY A/S | DTR | S76/69/770/81AS |  |  |  | CDC | 503 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S76 | 佳里一SS | 0 |  | 3M | #3MTR二次側(3M) |  | 51A | [17 empty] | 1-03-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.3M_51A | #3MTR二次側(3M) 51RY | DTR | S76/11/M3/51A |  |  |  | CDC | 504 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 2-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_TRA | #3MTR 重故障 | DTR | S76//3MTR/TRA |  |  |  | CDC | 505 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 2-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_TRF | #3MTR 輕故障 | DTR | S76//3MTR/TRF |  |  |  | CDC | 506 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 2-31-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_S/L | #3MTR OLTC S/L | DTR | S76//3MTR/SupLocal |  |  |  | CDC | 507 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 2-31-05 |  | 1-63 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_A/M | #3MTR OLTC A/M | DTR | S76//3MTR/Tap Chan |  |  |  | CDC | 508 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | OLTC_DLY | [17 empty] | 2-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_OLTC遲滯 | #3MTR OLTC遲滯 | DTR | S76//3MTR/OLTC_DLY |  |  |  | CDC | 509 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR_AC | #3MTR |  | FAULT | [17 empty] | 2-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_AC_FAULT | #3MTR AC電源失效 | DTR | S76//3MTR/AC_Fault |  |  |  | CDC | 510 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | CB | [17 empty] | 1-04-02 |  | 1-6C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.780_CB | 780(#4MTR) CB | DTR | S76/69/780/CB |  |  |  | CDC | 511 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 4M | #4MTR |  | CB | [17 empty] | 1-04-03 |  | 1-6D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.4M_CB | 4M(#4MTR) CB | DTR | S76/11/M4/CB |  |  |  | CDC | 512 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 51A | [17 empty] | 1-04-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_51A | #4MTR 51RY | DTR | S76/69/780/51A |  |  |  | CDC | 513 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 51NA | [17 empty] | 1-04-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_51NA | #4MTR 51N RY | DTR | S76/69/780/51NA |  |  |  | CDC | 514 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 51ZA | [17 empty] | 1-05-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_51ZA | #4MTR 51Z RY | DTR | S76//4MTR/51ZA |  |  |  | CDC | 515 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 1-05-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_87A | #4MTR 87RY | DTR | S76//4MTR/87A |  |  |  | CDC | 516 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 87UL | [17 empty] | 2-32-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_87UL | #4MTR 87RY U/L | DTR | S76//4MTR/87UL |  |  |  | CDC | 517 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | 4M | #4MTR二次側(4M) |  | 51A | [17 empty] | 1-05-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.4M_51A | #4MTR二次側(4M) 51RY | DTR | S76/11/M4/51A |  |  |  | CDC | 518 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 2-32-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_TRA | #4MTR 重故障 | DTR | S76//4MTR/TRA |  |  |  | CDC | 519 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 2-32-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_TRF | #4MTR 輕故障 | DTR | S76//4MTR/TRF |  |  |  | CDC | 520 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | SupLocal | [17 empty] | 2-32-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_S/L | #4MTR OLTC S/L | DTR | S76//4MTR/SupLocal |  |  |  | CDC | 521 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | A_M | [17 empty] | 2-32-05 |  | 1-77 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_A/M | #4MTR OLTC A/M | DTR | S76//4MTR/Tap Chan |  |  |  | CDC | 522 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | OLTC_DLY | [17 empty] | 2-32-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_OLTC遲滯 | #4MTR OLTC遲滯 | DTR | S76//4MTR/OLTC_DLY |  |  |  | CDC | 523 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR_AC | #4MTR |  | FAULT | [17 empty] | 2-32-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_AC_FAULT | #4MTR AC電源失效 | DTR | S76//4MTR/AC_Fault |  |  |  | CDC | 524 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | CB | [17 empty] | 1-05-06 |  | 2-00 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.790_CB | 790(#5MTR) CB | DTR | S76/69/790/CB |  |  |  | CDC | 525 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 5M | #5MTR |  | CB | [17 empty] | 1-05-07 |  | 2-01 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.5M_CB | 5M(#5MTR) CB | DTR | S76/11/M5/CB |  |  |  | CDC | 526 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 51A | [17 empty] | 1-06-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_51A | #5MTR 51RY | DTR | S76/69/790/51A |  |  |  | CDC | 527 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 51NA | [17 empty] | 1-06-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_51NA | #5MTR 51N RY | DTR | S76/69/790/51NA |  |  |  | CDC | 528 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 51ZA | [17 empty] | 1-07-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_51ZA | #5MTR 51Z RY | DTR | S76//5MTR/51ZA |  |  |  | CDC | 529 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 87A | [17 empty] | 1-06-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_87A | #5MTR 87RY | DTR | S76//5MTR/87A |  |  |  | CDC | 530 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 87UL | [17 empty] | 2-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_87UL | #5MTR 87RY U/L | DTR | S76//5MTR/87UL |  |  |  | CDC | 531 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 81AS | [17 empty] | 1-1F-06 |  | 2-11 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_81A/S | #5MTR 81RY A/S | DTR | S76/69/790/81AS |  |  |  | CDC | 532 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S76 | 佳里一SS | 0 |  | 5M | #5MTR二次側(5M) |  | 51A | [17 empty] | 1-06-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.5M_51A | #5MTR二次側(5M) 51RY | DTR | S76/11/M5/51A |  |  |  | CDC | 533 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | TRA | [17 empty] | 2-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_TRA | #5MTR 重故障 | DTR | S76//5MTR/TRA |  |  |  | CDC | 534 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | TRF | [17 empty] | 2-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_TRF | #5MTR 輕故障 | DTR | S76//5MTR/TRF |  |  |  | CDC | 535 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | SupLocal | [17 empty] | 2-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_S/L | #5MTR OLTC S/L | DTR | S76//5MTR/SupLocal |  |  |  | CDC | 536 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | A_M | [17 empty] | 2-33-05 |  | 2-0A | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_A/M | #5MTR OLTC A/M | DTR | S76//5MTR/Tap Chan |  |  |  | CDC | 537 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | OLTC_DLY | [17 empty] | 2-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_OLTC遲滯 | #5MTR OLTC遲滯 | DTR | S76//5MTR/OLTC_DLY |  |  |  | CDC | 538 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR_AC | #5MTR |  | FAULT | [17 empty] | 2-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_AC_FAULT | #5MTR AC電源失效 | DTR | S76//5MTR/AC_Fault |  |  |  | CDC | 539 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-13-07 |  | 1-33 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.210_CB | 210(11KV #1SC) CB | SC | S76/11/210/CB |  |  |  | CDC | 540 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.210_A/M | 11KV #1SC 乏控器 A/M | SC | S76/11/210/SC_A_M |  |  |  | CDC | 541 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-14-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.210_SCA | 11KV #1SC 51,51N RY | SC | S76/11/210/SCA |  |  |  | CDC | 542 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-15-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | S76/11/210/UVA |  |  |  | CDC | 543 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-16-05 |  | 1-48 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.220_CB | 220(11KV #2SC) CB | SC | S76/11/220/CB |  |  |  | CDC | 544 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-30-06 |  | 1-50 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.220_A/M | 11KV #2SC 乏控器 A/M | SC | S76/11/220/SC_A_M |  |  |  | CDC | 545 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.220_SCA | 11KV #2SC 51,51N RY | SC | S76/11/220/SCA |  |  |  | CDC | 546 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-17-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | S76/11/220/UVA |  |  |  | CDC | 547 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-19-03 |  | 1-5C | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.230_CB | 230(11KV #3SC) CB | SC | S76/11/230/CB |  |  |  | CDC | 548 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-31-06 |  | 1-64 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.230_A/M | 11KV #3SC 乏控器 A/M | SC | S76/11/230/SC_A_M |  |  |  | CDC | 549 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-1A-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.230_SCA | 11KV #3SC 51,51N RY | SC | S76/11/230/SCA |  |  |  | CDC | 550 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | S76/11/230/UVA |  |  |  | CDC | 551 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-1C-02 |  | 1-70 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.240_CB | 240(11KV #4SC) CB | SC | S76/11/240/CB |  |  |  | CDC | 552 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-32-06 |  | 1-78 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.240_A/M | 11KV #4SC 乏控器 A/M | SC | S76/11/240/SC_A_M |  |  |  | CDC | 553 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-1D-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.240_SCA | 11KV #4SC 51,51N RY | SC | S76/11/240/SCA |  |  |  | CDC | 554 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-1D-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | S76/11/240/UVA |  |  |  | CDC | 555 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-1F-00 |  | 2-03 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.250_CB | 250(11KV #5SC) CB | SC | S76/11/250/CB |  |  |  | CDC | 556 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-33-06 |  | 2-0B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.250_A/M | 11KV #5SC 乏控器 A/M | SC | S76/11/250/SC_A_M |  |  |  | CDC | 557 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-1F-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.250_SCA | 11KV #5SC 51,51N RY | SC | S76/11/250/SCA |  |  |  | CDC | 558 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-10-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.250_UVA | 11KV #5SC 27RY(欠壓) | SC | S76/11/250/UVA |  |  |  | CDC | 559 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-13-04 |  | 1-08 | [5 empty] | 69KV_N | [8 empty] | 佳一SS.810_CB | 810(69KV #1SC) CB | SC | S76/69/810/CB |  |  |  | CDC | 560 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-13-05 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.810_SCA | 69KV #1SC 51,51N RY | SC | S76/69/810/SCA |  |  |  | CDC | 561 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-13-06 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.810_OUVA | 69KV #1SC 27,59RY | SC | S76/69/810/UVA |  |  |  | CDC | 562 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | S76/69/1BUS/BUS_VUA |  |  |  | CDC | 563 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S76/11/ComPoint/CBA |  |  |  | CDC | 564 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S76/11/ComPoint/CBF |  |  |  | CDC | 565 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S76/69/ComPoint/ABS_89A |  |  |  | CDC | 566 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S76/69/ComPoint/CBA |  |  |  | CDC | 567 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S76/69/ComPoint/CBF |  |  |  | CDC | 568 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S76/0/RTU/RTU_R_L |  |  |  | CDC | 569 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S76 | 佳里一SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.TEST_CB | TEST CB | OTHER | S76/0/RTU/Test_CB |  |  |  | CDC | 570 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S76/0/StaDev/PSF |  |  |  | CDC | 571 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-33-13 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S76/0/StaDev/ACB1 |  |  |  | CDC | 572 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S76 | 佳里一SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-33-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S76/0/StaDev/ACB2 |  |  |  | CDC | 573 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S76 | 佳里一SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S76/0/StaDev/STUV |  |  |  | CDC | 574 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.直流充電機故障 | 直流充電機故障 | OTHER | S76/0/StaDev/CHG1 |  |  |  | CDC | 575 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S76/0/StaDev/DCA |  |  |  | CDC | 576 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S76/0/StaDev/DCE |  |  |  | CDC | 577 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S76/0/StaDev/OilLeak |  |  |  | CDC | 578 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | SUBA | [17 empty] | 2-35-13 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S76/0/StaDev/5A5Other |  |  |  | CDC | 579 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | SUBF | [17 empty] | 2-35-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S76/0/StaDev/6A5Other |  |  |  | CDC | 580 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 2-35-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S76/0/StaDev/7A5Other |  |  |  | CDC | 581 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S76/0/StaDev/CHG2 |  |  |  | CDC | 582 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | CommACF | [17 empty] | 2-35-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S76/0/StaDev/CommACF |  |  |  | CDC | 583 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.無人化門禁(1) | 無人化門禁(1)門禁保全 | OTHER | S76/0/StaDev/Door1 |  |  |  | CDC | 584 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S76 | 佳里一SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S76/0/StaDev/Lights1 |  |  |  | CDC | 585 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S76 | 佳里一SS | 0 |  | 1_MAIN | #1MCB |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1_MAIN_51NA | #1MCB GDA | OTHER | S76/11/M1/51NA |  |  |  | CDC | 586 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3_MAIN | #3MCB |  | 51NA | [17 empty] | 1-03-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3_MAIN_51NA | #3MCB GDA | OTHER | S76/11/M3/51NA |  |  |  | CDC | 587 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4_MAIN | #4MCB |  | 51NA | [17 empty] | 1-05-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4_MAIN_51NA | #4MCB GDA | OTHER | S76/11/M4/51NA |  |  |  | CDC | 588 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5_MAIN | #5MCB |  | 51NA | [17 empty] | 1-06-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5_MAIN_51NA | #5MCB GDA | OTHER | S76/11/M5/51NA |  |  |  | CDC | 589 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.69KVSC警報 | 69KVSC警報 | OTHER | S76/69/810/60A |  |  |  | CDC | 590 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.RTU_DC故障 | RTU DC故障 | OTHER | S76/0/RTU/DCA |  |  |  | CDC | 591 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 水氣霧故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.水氣霧故障 | 水氣霧故障 | OTHER | S76/0/StaDev/2A5Other |  |  |  | CDC | 592 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 水氣霧警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.水氣霧警報 | 水氣霧警報 | OTHER | S76/0/StaDev/3A5Other |  |  |  | CDC | 593 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | Fire | [17 empty] | 1-30-10 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.火災警報 | 火警 | OTHER | S76/0/StaDev/Fire |  |  |  | CDC | 594 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.安全監控 | 保全設定 | OTHER | S76/0/StaDev/1A5Other |  |  |  | CDC | 595 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.門禁小門 | 門禁小門 | OTHER | S76/0/StaDev/Door2 |  |  |  | CDC | 596 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S76/0/StaDev/Lights2 |  |  |  | CDC | 597 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | PHA | [17 empty] | 1-10-06 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.650_PHA | 佳里麻豆線(650) 相間RY | LINE69 | S76/69/650/PHA |  |  |  | CDC | 598 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | GDA | [17 empty] | 1-10-07 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.650_GDA | 佳里麻豆線(650) 接地RY | LINE69 | S76/69/650/GDA |  |  |  | CDC | 599 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | CB | [17 empty] | 1-10-04 |  | 1-02 | [5 empty] | 69KV_N | [8 empty] | 佳一SS.650_CB | 650(佳里麻豆線) CB | LINE69 | S76/69/650/CB |  |  |  | CDC | 600 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-1D-01 |  | 1-7E | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S76/0/StaDev/4A5Other |  |  |  | CDC | 601 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.730_PHA | 學甲佳里一路(730) 相間RY | LINE69 | S76/69/730/PHA |  |  |  | CDC | 602 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.730_GDA | 學甲佳里一路(730) 接地RY | LINE69 | S76/69/730/GDA |  |  |  | CDC | 603 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | CB | [17 empty] | 1-11-00 |  | 1-03 | [5 empty] | 69KV_N | [8 empty] | 佳一SS.730_CB | 730(學甲佳里一路) CB | LINE69 | S76/69/730/CB |  |  |  | CDC | 604 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 620 | 學甲佳里二路(620) |  | 87A | [17 empty] | 1-10-01 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.620_87A | 學甲佳里二路(620) 87RY | OTHER | S76/69/620/87A |  |  |  | CDC | 605 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 620 | 學甲佳里二路(620) |  | 87UL | [17 empty] | 1-32-00 |  | 1-09 | [5 empty] | ADCS_N | [8 empty] | 佳一SS.620_87UL | 學甲佳里二路(620) 87RY U/L | OTHER | S76/69/620/87UL |  |  |  | CDC | 606 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S76/69/ComPoint/CFA |  |  |  | CDC | 607 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_IED_FA | 69KV IED故障 | OTHER | S76/69/ComPoint/IRFA |  |  |  | CDC | 608 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 730 | 學甲佳里一路(730) |  | 87A | [17 empty] | 1-11-01 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.730_87A | 730學甲佳里一路87RY | OTHER | S76/69/730/87A |  |  |  | CDC | 609 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 730 | 學甲佳里一路(730) |  | 87UL | [17 empty] | 1-32-04 |  | 1-0B | [5 empty] | 69KV_N | [8 empty] | 佳一SS.730_87UL | 730學甲佳里一路87RY UL | OTHER | S76/69/730/87UL |  |  |  | CDC | 610 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.11KV_IED_FA | 11KV IED故障 | OTHER | S76/11/ComPoint/IRFA |  |  |  | CDC | 611 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-13 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.81RY_IED_FA | 低頻IED故障 | OTHER | S76/0/StaDev/81A_RYFA |  |  |  | CDC | 612 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.PM_CFA | PM通訊故障 | OTHER | S76/0/StaDev/PMA |  |  |  | CDC | 613 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-0C-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_63Q | #1MTR ULTC電驛動作 | OTHER | S76//1MTR/63Q |  |  |  | CDC | 614 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-0C-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_96B1 | #1MTR 撲氣電驛警報 | OTHER | S76//1MTR/96B1 |  |  |  | CDC | 615 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-0C-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_96B2 | #1MTR 撲氣電驛動作 | OTHER | S76//1MTR/96B2 |  |  |  | CDC | 616 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-0C-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_96D | #1MTR 放壓電驛動作 | OTHER | S76//1MTR/96D |  |  |  | CDC | 617 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-0C-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_96P | #1MTR 突壓電驛動作 | OTHER | S76//1MTR/96P |  |  |  | CDC | 618 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_63Q | #2MTR ULTC電驛動作 | OTHER | S76//2MTR/63Q |  |  |  | CDC | 619 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-0D-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_96B1 | #2MTR 撲氣電驛警報 | OTHER | S76//2MTR/96B1 |  |  |  | CDC | 620 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-0D-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_96B2 | #2MTR 撲氣電驛動作 | OTHER | S76//2MTR/96B2 |  |  |  | CDC | 621 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-0C-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_96D | #2MTR 放壓電驛動作 | OTHER | S76//2MTR/96D |  |  |  | CDC | 622 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-0C-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_96P | #2MTR 突壓電驛動作 | OTHER | S76//2MTR/96P |  |  |  | CDC | 623 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-0D-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_63Q | #3MTR ULTC電驛動作 | OTHER | S76//3MTR/63Q |  |  |  | CDC | 624 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-0D-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_96B1 | #3MTR 撲氣電驛警報 | OTHER | S76//3MTR/96B1 |  |  |  | CDC | 625 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-0D-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_96B2 | #3MTR 撲氣電驛動作 | OTHER | S76//3MTR/96B2 |  |  |  | CDC | 626 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-0D-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_96D | #3MTR 放壓電驛動作 | OTHER | S76//3MTR/96D |  |  |  | CDC | 627 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-0D-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_96P | #3MTR 突壓電驛動作 | OTHER | S76//3MTR/96P |  |  |  | CDC | 628 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 63Q | [17 empty] | 1-0E-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_63Q | #4MTR ULTC電驛動作 | OTHER | S76//4MTR/63Q |  |  |  | CDC | 629 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 96B1 | [17 empty] | 1-0E-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_96B1 | #4MTR 撲氣電驛警報 | OTHER | S76//4MTR/96B1 |  |  |  | CDC | 630 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 96B2 | [17 empty] | 1-0E-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_96B2 | #4MTR 撲氣電驛動作 | OTHER | S76//4MTR/96B2 |  |  |  | CDC | 631 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 96D | [17 empty] | 1-0D-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_96D | #4MTR 放壓電驛動作 | OTHER | S76//4MTR/96D |  |  |  | CDC | 632 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 96P | [17 empty] | 1-0E-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_96P | #4MTR 突壓電驛動作 | OTHER | S76//4MTR/96P |  |  |  | CDC | 633 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 63Q | [17 empty] | 1-0E-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_63Q | #5MTR ULTC電驛動作 | OTHER | S76//5MTR/63Q |  |  |  | CDC | 634 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 96B1 | [17 empty] | 1-0E-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_96B1 | #5MTR 撲氣電驛警報 | OTHER | S76//5MTR/96B1 |  |  |  | CDC | 635 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 96B2 | [17 empty] | 1-0F-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_96B2 | #5MTR 撲氣電驛動作 | OTHER | S76//5MTR/96B2 |  |  |  | CDC | 636 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 96D | [17 empty] | 1-0E-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_96D | #5MTR 放壓電驛動作 | OTHER | S76//5MTR/96D |  |  |  | CDC | 637 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 96P | [17 empty] | 1-0E-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_96P | #5MTR 突壓電驛動作 | OTHER | S76//5MTR/96P |  |  |  | CDC | 638 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.變電所低水位 | 變電所低水位 | OTHER | S76/0/StaDev/Water1 |  |  |  | CDC | 639 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.變電所高水位 | 變電所高水位 | OTHER | S76/0/StaDev/Water |  |  |  | CDC | 640 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | PHA | [17 empty] | 2-13-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_PHA | 11KV備01線(KN01) 相間RY | FEEDER | S76/11/KN01/PHA |  |  |  | CDC | 641 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) |  | GDA | [17 empty] | 2-13-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_GDA | 11KV備01線(KN01) 接地RY | FEEDER | S76/11/KN01/GDA |  |  |  | CDC | 642 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) 79RY |  | 79UL | [17 empty] | 2-30-13 |  | 2-15 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_79UL | 11KV備01線(KN01) 79RY U/L | FEEDER | S76/11/KN01/79UL |  |  |  | CDC | 643 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN01 | 備01線(KN01) LCO分流器 |  | ADJ | [17 empty] | 2-35-09 |  | 2-31 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_ADJ | 11KV備01線(KN01) LCO分流器 U/L | FEEDER | S76/11/KN01/ADJ |  |  |  | CDC | 644 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN01 | KN01(11KV備01線) |  | CB | [17 empty] | 2-13-00 |  | 2-13 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_CB | KN01(11KV備01線) CB | FEEDER | S76/11/KN01/CB |  |  |  | CDC | 645 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-13-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1SSTR_51A | #1SSTR 51RY | OTHER | S76/11/390/PHA |  |  |  | CDC | 646 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-13-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | S76/11/390/GDA |  |  |  | CDC | 647 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 2-36-00 | 2-36-01 | 1-20 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.751_DS | 751(#1MTR) DS | DTR | S76/69/750/DS1 |  |  |  | CDC | 648 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 2-36-02 | 2-36-03 | 1-21 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.752_DS | 752(#1MTR) DS | DTR | S76/69/750/DS2 |  |  |  | CDC | 649 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1MTR_96PA | #1MTR 機械保護動作 | DTR | S76//1MTR/96PA |  |  |  | CDC | 650 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2MTR_96PA | #2MTR 機械保護動作 | DTR | S76//2MTR/96PA |  |  |  | CDC | 651 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-03-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#3MTR_96PA | #3MTR 機械保護動作 | DTR | S76//3MTR/96PA |  |  |  | CDC | 652 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 4MTR | #4MTR |  | 96PA | [17 empty] | 1-04-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#4MTR_96PA | #4MTR 機械保護動作 | DTR | S76//4MTR/96PA |  |  |  | CDC | 653 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 5MTR | #5MTR |  | 96PA | [17 empty] | 1-06-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#5MTR_96PA | #5MTR 機械保護動作 | DTR | S76//5MTR/96PA |  |  |  | CDC | 654 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1M | #1MTR |  | 81A | [17 empty] | 1-1B-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.1M_81A | 1M(#1MTR) 81RY | OTHER | S76/11/M1/81A |  |  |  | CDC | 655 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 1M | #1MTR |  | 81UL | [17 empty] | 1-33-15 |  | 1-43 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.1M_81UL | 1M(#1MTR) 81RY U/L | OTHER | S76/11/M1/81UL |  |  |  | CDC | 656 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | KN01 | KN01 |  | 81A | [17 empty] | 2-13-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_81A | KN01 81RY | OTHER | S76/11/KN01/81A |  |  |  | CDC | 657 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN01 | 備01線 |  | LOA | [17 empty] | 1-3C-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_LOA | 備01線 復閉失敗閉鎖 | OTHER | S76/11/KN01/LOA |  |  |  | CDC | 658 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN21 | KN21 |  | 81A | [17 empty] | 2-11-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_81A | KN21 81RY | OTHER | S76/11/KN21/81A |  |  |  | CDC | 659 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN21 | 漚汪線 |  | LOA | [17 empty] | 1-3E-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_LOA | 漚汪線 復閉失敗閉鎖 | OTHER | S76/11/KN21/LOA |  |  |  | CDC | 660 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN22 | KN22 |  | 81A | [17 empty] | 2-11-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_81A | KN22 81RY | OTHER | S76/11/KN22/81A |  |  |  | CDC | 661 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN22 | 佳興線 |  | LOA | [17 empty] | 1-3E-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_LOA | 佳興線 復閉失敗閉鎖 | OTHER | S76/11/KN22/LOA |  |  |  | CDC | 662 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN23 | KN23 |  | 81A | [17 empty] | 2-12-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_81A | KN23 81RY | OTHER | S76/11/KN23/81A |  |  |  | CDC | 663 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN23 | 佳工線 |  | LOA | [17 empty] | 1-3E-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_LOA | 佳工線 復閉失敗閉鎖 | OTHER | S76/11/KN23/LOA |  |  |  | CDC | 664 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN24 | KN24 |  | 81A | [17 empty] | 2-12-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_81A | KN24 81RY | OTHER | S76/11/KN24/81A |  |  |  | CDC | 665 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN24 | 通吉線 |  | LOA | [17 empty] | 1-3E-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_LOA | 通吉線 復閉失敗閉鎖 | OTHER | S76/11/KN24/LOA |  |  |  | CDC | 666 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN25 | KN25 |  | 81A | [17 empty] | 2-12-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_81A | KN25 81RY | OTHER | S76/11/KN25/81A |  |  |  | CDC | 667 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN25 | 佳25線 |  | LOA | [17 empty] | 1-3E-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_LOA | 佳25線 復閉失敗閉鎖 | OTHER | S76/11/KN25/LOA |  |  |  | CDC | 668 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-12-00 |  | 1-07 | [5 empty] | 69KV_N | [8 empty] | 佳一SS.600_CB | 600(TIE) CB | TIE | S76/69/600/CB |  |  |  | CDC | 669 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 2-37-04 | 2-37-05 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 佳一SS.601_DS | 601(TIE) DS | TIE | S76/69/600/DS1 |  |  |  | CDC | 670 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 2-37-06 | 2-37-07 | 1-1D | [5 empty] | ADCS_N | [8 empty] | 佳一SS.602_DS | 602(TIE) DS | TIE | S76/69/600/DS2 |  |  |  | CDC | 671 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | S76/69/2BUS/BUS_VUA |  |  |  | CDC | 672 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | 600GDA(1) | [17 empty] | 1-12-02 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.600GDA(1) | 69KV #1BUS TIE(600) 67N | OTHER | S76/69/600/GDA1 |  |  |  | CDC | 673 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 2BUS | #2BUS |  | 600GDA(2) | [17 empty] | 1-12-04 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.600GDA(2) | 69KV #2BUS TIE(600) 67N | OTHER | S76/69/600/GDA2 |  |  |  | CDC | 674 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | 600PHA(1) | [17 empty] | 1-12-01 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.600PHA(1) | 69KV #1BUS TIE(600) 67 | OTHER | S76/69/600/PHA1 |  |  |  | CDC | 675 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 2BUS | #2BUS |  | 600PHA(2) | [17 empty] | 1-12-03 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.600PHA(2) | 69KV #2BUS TIE(600) 67 | OTHER | S76/69/600/PHA2 |  |  |  | CDC | 676 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | 87A | [17 empty] | 1-12-05 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.69KV1BUS_87A | 69KV #1BUS 87B1A | OTHER | S76/69/1BUS/87A |  |  |  | CDC | 677 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 1BUS | #1BUS |  | 87UL | [17 empty] | 1-32-08 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 佳一SS.69KV1BUS_87UL | 69KV #1BUS 87RY UL | OTHER | S76/69/1BUS/87UL |  |  |  | CDC | 678 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | 2BUS | #2BUS |  | 87A | [17 empty] | 1-12-06 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.69KV2BUS_87A | 69KV #2BUS 87B2A | OTHER | S76/69/2BUS/87A |  |  |  | CDC | 679 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 2BUS | #2BUS |  | 87UL | [17 empty] | 1-32-09 |  | 1-0E | [5 empty] | ADCS_N | [8 empty] | 佳一SS.69KV2BUS_87UL | 69KV #2BUS 87RY UL | OTHER | S76/69/2BUS/87UL |  |  |  | CDC | 680 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | S76/69/ComPoint/12B_CTFA |  |  |  | CDC | 681 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_BUS_RYFA | 69KV BUS IED故障 | OTHER | S76/69/ComPoint/BUS_RYFA |  |  |  | CDC | 682 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | _TIE | TIE |  | RYFA | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 佳一SS.69KV_TIE_RYFA | 69KV TIE IED故障 | OTHER | S76/69/600/RYFA |  |  |  | CDC | 683 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 650 | 佳里麻豆線(650) |  | 87A | [17 empty] | 1-10-05 | [7 empty] | 69KV_N | [8 empty] | 佳一SS.650_87A | 650麻豆佳里線87RY | OTHER | S76/69/650/87A |  |  |  | CDC | 684 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 650 | 佳里麻豆線(650) |  | 87UL | [17 empty] | 1-32-02 |  | 1-0A | [5 empty] | ADCS_N | [8 empty] | 佳一SS.650_87UL | 650麻豆佳里線87RY UL | OTHER | S76/69/650/87UL |  |  |  | CDC | 685 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | PHA | [17 empty] | 2-13-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_PHA | 11KV備02線(KN02) 相間RY | FEEDER | S76/11/KN02/PHA |  |  |  | CDC | 686 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) |  | GDA | [17 empty] | 2-13-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_GDA | 11KV備02線(KN02) 接地RY | FEEDER | S76/11/KN02/GDA |  |  |  | CDC | 687 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-16 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_79UL | 11KV備02線(KN02) 79RY U/L | FEEDER | S76/11/KN02/79UL |  |  |  | CDC | 688 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 11 | 11kV | KN02 | 備02線(KN02) LCO分流器 |  | ADJ | [17 empty] | 2-35-10 |  | 2-32 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_ADJ | 11KV備02線(KN02) LCO分流器 U/L | FEEDER | S76/11/KN02/ADJ |  |  |  | CDC | 689 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S76 | 佳里一SS | 11 | 11kV | KN02 | KN02(11KV備02線) |  | CB | [17 empty] | 2-13-04 |  | 2-14 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_CB | KN02(11KV備02線) CB | FEEDER | S76/11/KN02/CB |  |  |  | CDC | 690 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-13-01 |  | 1-42 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.390_CB | 390(#1SSTR) CB | OTHER | S76/11/390/CB |  |  |  | CDC | 691 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2MA | #2MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MA_CB | 2MA(#2MTR) CB | DTR | S76/11/M2A/CB |  |  |  | CDC | 692 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2MB | #2MTR |  | CB | [17 empty] | 1-01-04 |  | 1-46 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MB_CB | 2MB(#2MTR) CB | DTR | S76/11/M2B/CB |  |  |  | CDC | 693 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2MA | #2MTR二次側(2MA) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MA_51A | #2MTR二次側(2MA) 51RY | DTR | S76/11/M2A/51A |  |  |  | CDC | 694 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MB | #2MTR二次側(2MB) |  | 51A | [17 empty] | 1-02-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MB_51A | #2MTR二次側(2MB) 51RY | DTR | S76/11/M2B/51A |  |  |  | CDC | 695 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2_MA | #2MA |  | 51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2_MA_51NA | #2MA GDA | OTHER | S76/11/M2A/51NA |  |  |  | CDC | 696 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2_MB | #2MB |  | 51NA | [17 empty] | 1-02-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2_MB_51NA | #2MB GDA | OTHER | S76/11/M2B/51NA |  |  |  | CDC | 697 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MA | #2MTR |  | 81A | [17 empty] | 1-12-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MA_81A | 2MA(#2MTR) 81RY | OTHER | S76/11/M2A/81A |  |  |  | CDC | 698 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MA | #2MTR |  | 81UL | [17 empty] | 2-31-14 |  | 1-57 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MA_81UL | 2MA(#2MTR) 81RY U/L | OTHER | S76/11/M2A/81UL |  |  |  | CDC | 699 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | 2MB | #2MTR |  | 81A | [17 empty] | 1-13-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MB_81A | 2MB(#2MTR) 81RY | OTHER | S76/11/M2B/81A |  |  |  | CDC | 700 | GENERICDIPoint | SS417_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | 2MB | #2MTR |  | 81UL | [17 empty] | 2-31-15 |  | 1-6B | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MB_81UL | 2MB(#2MTR) 81RY U/L | OTHER | S76/11/M2B/81UL |  |  |  | CDC | 701 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S76 | 佳里一SS | 0 |  | KN02 | KN02 |  | 81A | [17 empty] | 2-13-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_81A | KN02 81RY | OTHER | S76/11/KN02/81A |  |  |  | CDC | 702 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN02 | 備02線 |  | LOA | [17 empty] | 1-3F-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_LOA | 備02線 復閉失敗閉鎖 | OTHER | S76/11/KN02/LOA |  |  |  | CDC | 703 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN26 | KN26 |  | 81A | [17 empty] | 2-12-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_81A | KN26 81RY | OTHER | S76/11/KN26/81A |  |  |  | CDC | 704 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN26 | 漳洲線 |  | LOA | [17 empty] | 1-3E-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_LOA | 漳洲線 復閉失敗閉鎖 | OTHER | S76/11/KN26/LOA |  |  |  | CDC | 705 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN27 | KN27 |  | 81A | [17 empty] | 2-12-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_81A | KN27 81RY | OTHER | S76/11/KN27/81A |  |  |  | CDC | 706 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN27 | 頂城線 |  | LOA | [17 empty] | 1-3E-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_LOA | 頂城線 復閉失敗閉鎖 | OTHER | S76/11/KN27/LOA |  |  |  | CDC | 707 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN28 | KN28 |  | 81A | [17 empty] | 2-12-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_81A | KN28 81RY | OTHER | S76/11/KN28/81A |  |  |  | CDC | 708 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN28 | 七股線 |  | LOA | [17 empty] | 1-3E-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_LOA | 七股線 復閉失敗閉鎖 | OTHER | S76/11/KN28/LOA |  |  |  | CDC | 709 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN29 | KN29 |  | 81A | [17 empty] | 2-12-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_81A | KN29 81RY | OTHER | S76/11/KN29/81A |  |  |  | CDC | 710 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN29 | 塭寮線 |  | LOA | [17 empty] | 1-3E-08 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_LOA | 塭寮線 復閉失敗閉鎖 | OTHER | S76/11/KN29/LOA |  |  |  | CDC | 711 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN30 | KN30 |  | 81A | [17 empty] | 2-12-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_81A | KN30 81RY | OTHER | S76/11/KN30/81A |  |  |  | CDC | 712 | GENERICDIPoint | SS417_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN30 | 佳30線 |  | LOA | [17 empty] | 1-3E-09 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_LOA | 佳30線 復閉失敗閉鎖 | OTHER | S76/11/KN30/LOA |  |  |  | CDC | 713 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | [16 empty] | 2-37-08 | 2-37-09 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 佳一SS.811_DS | 811(69KV #1SC) DS | SC | S76/69/810/DS1 |  |  |  | CDC | 714 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | [16 empty] | 2-37-10 | 2-37-11 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 佳一SS.812_DS | 812(69KV #1SC) DS | SC | S76/69/810/DS2 |  |  |  | CDC | 715 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | DS1 | 621 | [16 empty] | 2-38-00 | 2-38-01 | 2-34 | [5 empty] | ADCS_N | [8 empty] | 佳一SS.621_DS | 621(學甲佳里二路) DS | LINE69 | S76/69/620/DS1 |  |  |  | CDC | 716 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | DS2 | 622 | [16 empty] | 2-38-02 | 2-38-03 | 2-35 | [5 empty] | ADCS_N | [8 empty] | 佳一SS.622_DS | 622(學甲佳里二路) DS | LINE69 | S76/69/620/DS2 |  |  |  | CDC | 717 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | DS3 | 623 | [16 empty] | 2-38-04 | 2-38-05 | 2-36 | [5 empty] | ADCS_N | [8 empty] | 佳一SS.623_DS | 623(學甲佳里二路) DS | LINE69 | S76/69/620/DS3 |  |  |  | CDC | 718 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | E3 | 623E | [16 empty] | 2-38-06 | 2-38-07 | 2-37 | [5 empty] | ADCS_N | [8 empty] | 佳一SS.623E_ES | 623E(學甲佳里二路) ES | LINE69 | S76/69/620/ES3 |  |  |  | CDC | 719 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 0 |  | KN31 | 西港線 |  | LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_LOA | 西港線 復閉失敗閉鎖 | OTHER | S76/11/KN31/LOA |  |  |  | CDC | 720 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN32 | 子良線 |  | LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_LOA | 子良線 復閉失敗閉鎖 | OTHER | S76/11/KN32/LOA |  |  |  | CDC | 721 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN33 | 嘉福線 |  | LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_LOA | 嘉福線 復閉失敗閉鎖 | OTHER | S76/11/KN33/LOA |  |  |  | CDC | 722 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN34 | 篤加線 |  | LOA | [17 empty] | 1-3F-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_LOA | 篤加線 復閉失敗閉鎖 | OTHER | S76/11/KN34/LOA |  |  |  | CDC | 723 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN35 | 林樂線 |  | LOA | [17 empty] | 1-3F-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_LOA | 林樂線 復閉失敗閉鎖 | OTHER | S76/11/KN35/LOA |  |  |  | CDC | 724 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN36 | 三股線 |  | LOA | [17 empty] | 1-3F-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_LOA | 三股線 復閉失敗閉鎖 | OTHER | S76/11/KN36/LOA |  |  |  | CDC | 725 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN37 | 佳塭線 |  | LOA | [17 empty] | 1-3F-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_LOA | 佳塭線 復閉失敗閉鎖 | OTHER | S76/11/KN37/LOA |  |  |  | CDC | 726 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN38 | 光復線 |  | LOA | [17 empty] | 1-3F-08 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_LOA | 光復線 復閉失敗閉鎖 | OTHER | S76/11/KN38/LOA |  |  |  | CDC | 727 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN39 | 新生線 |  | LOA | [17 empty] | 1-3F-09 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_LOA | 新生線 復閉失敗閉鎖 | OTHER | S76/11/KN39/LOA |  |  |  | CDC | 728 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN40 | 仁愛線 |  | LOA | [17 empty] | 1-3F-10 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_LOA | 仁愛線 復閉失敗閉鎖 | OTHER | S76/11/KN40/LOA |  |  |  | CDC | 729 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN41 | 北農線 |  | LOA | [17 empty] | 1-3F-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_LOA | 北農線 復閉失敗閉鎖 | OTHER | S76/11/KN41/LOA |  |  |  | CDC | 730 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN42 | 中山線 |  | LOA | [17 empty] | 1-3F-13 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_LOA | 中山線 復閉失敗閉鎖 | OTHER | S76/11/KN42/LOA |  |  |  | CDC | 731 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN43 | 佳麻線 |  | LOA | [17 empty] | 1-3F-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_LOA | 佳麻線 復閉失敗閉鎖 | OTHER | S76/11/KN43/LOA |  |  |  | CDC | 732 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN44 | 佳西線 |  | LOA | [17 empty] | 1-3F-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_LOA | 佳西線 復閉失敗閉鎖 | OTHER | S76/11/KN44/LOA |  |  |  | CDC | 733 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 0 |  | KN45 | 佳45線 |  | LOA | [17 empty] | 1-3F-11 | [7 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_LOA | 佳45線 復閉失敗閉鎖 | OTHER | S76/11/KN45/LOA |  |  |  | CDC | 734 | GENERICDIPoint | SS417_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | DS1 | 731 | [16 empty] | 2-39-00 | 2-39-01 | 2-3C | [5 empty] | ADCS_N | [8 empty] | 佳一SS.731_DS | 731(學甲佳里一路) DS | LINE69 | S76/69/730/DS1 |  |  |  | CDC | 735 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | DS2 | 732 | [16 empty] | 2-39-02 | 2-39-03 | 2-3D | [5 empty] | ADCS_N | [8 empty] | 佳一SS.732_DS | 732(學甲佳里一路) DS | LINE69 | S76/69/730/DS2 |  |  |  | CDC | 736 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | DS3 | 733 | [16 empty] | 2-39-04 | 2-39-05 | 2-3E | [5 empty] | ADCS_N | [8 empty] | 佳一SS.733_DS | 733(學甲佳里一路) DS | LINE69 | S76/69/730/DS3 |  |  |  | CDC | 737 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | E3 | 733E | [16 empty] | 2-39-06 | 2-39-07 | 2-3F | [5 empty] | ADCS_N | [8 empty] | 佳一SS.733E_ES | 733E(學甲佳里一路) ES | LINE69 | S76/69/730/ES3 |  |  |  | CDC | 738 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | DS1 | 791 | [16 empty] | 2-37-00 | 2-37-01 | 1-28 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.791_DS | 791(#5MTR) DS | DTR | S76/69/790/DS1 |  |  |  | CDC | 739 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | DS2 | 792 | [16 empty] | 2-37-02 | 2-37-03 | 1-29 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.792_DS | 792(#5MTR) DS | DTR | S76/69/790/DS2 |  |  |  | CDC | 740 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | DS1 | 781 | [16 empty] | 2-36-12 | 2-36-13 | 1-26 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.781_DS | 781(#4MTR) DS | DTR | S76/69/780/DS1 |  |  |  | CDC | 741 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | DS2 | 782 | [16 empty] | 2-36-14 | 2-36-15 | 1-27 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.782_DS | 782(#4MTR) DS | DTR | S76/69/780/DS2 |  |  |  | CDC | 742 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 2-36-04 | 2-36-05 | 1-22 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.761_DS | 761(#2MTR) DS | DTR | S76/69/760/DS1 |  |  |  | CDC | 743 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 2-36-06 | 2-36-07 | 1-23 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.762_DS | 762(#2MTR) DS | DTR | S76/69/760/DS2 |  |  |  | CDC | 744 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | DS1 | 651 | [16 empty] | 2-38-08 | 2-38-09 | 2-38 | [5 empty] | ADCS_N | [8 empty] | 佳一SS.651_DS | 651(佳里麻豆線) DS | LINE69 | S76/69/650/DS1 |  |  |  | CDC | 745 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | DS2 | 652 | [16 empty] | 2-38-10 | 2-38-11 | 2-39 | [5 empty] | ADCS_N | [8 empty] | 佳一SS.652_DS | 652(佳里麻豆線) DS | LINE69 | S76/69/650/DS2 |  |  |  | CDC | 746 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | DS3 | 653 | [16 empty] | 2-38-12 | 2-38-13 | 2-3A | [5 empty] | ADCS_N | [8 empty] | 佳一SS.653_DS | 653(佳里麻豆線) DS | LINE69 | S76/69/650/DS3 |  |  |  | CDC | 747 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | E3 | 653E | [16 empty] | 2-38-14 | 2-38-15 | 2-3B | [5 empty] | ADCS_N | [8 empty] | 佳一SS.653E_ES | 653E(佳里麻豆線) ES | LINE69 | S76/69/650/ES3 |  |  |  | CDC | 748 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | [16 empty] | 2-36-08 | 2-36-09 | 1-24 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.771_DS | 771(#3MTR) DS | DTR | S76/69/770/DS1 |  |  |  | CDC | 749 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | [16 empty] | 2-36-10 | 2-36-11 | 1-25 | [5 empty] | DDCS4_2 | [8 empty] | 佳一SS.772_DS | 772(#3MTR) DS | DTR | S76/69/770/DS2 |  |  |  | CDC | 750 | GENERICDIPoint | SS417_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S76 | 佳里一SS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.210_SC_CAP | 11KV#1SC 容量 | SC | S76/11/210/1AI_Oth |  |  |  |  | 751 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.220_SC_CAP | 11KV#2SC 容量 | SC | S76/11/220/2AI_Oth |  |  |  |  | 752 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.230_SC_CAP | 11KV#3SC 容量 | SC | S76/11/230/3AI_Oth |  |  |  |  | 753 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.240_SC_CAP | 11KV#4SC 容量 | SC | S76/11/240/4AI_Oth |  |  |  |  | 754 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 11 | 11kV | 250_SC | #5SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.250_SC_CAP | 11KV#5SC 容量 | SC | [5 empty] | 755 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 69 | 69kV | 810_SC | #1SC | 10.8 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳一SS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 756 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.620LE | 620LE (非取樣點) | LINE69 | S76/69/620/LE0 |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN21 | KN21_ES |  | LE0 | KN21_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_ES | KN21_ES (非取樣點) | FEEDER | S76/11/KN21/ES |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN22 | KN22_ES |  | LE0 | KN22_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_ES | KN22_ES (非取樣點) | FEEDER | S76/11/KN22/ES |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN23 | KN23_ES |  | LE0 | KN23_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_ES | KN23_ES (非取樣點) | FEEDER | S76/11/KN23/ES |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN24 | KN24_ES |  | LE0 | KN24_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_ES | KN24_ES (非取樣點) | FEEDER | S76/11/KN24/ES |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN26 | KN26_ES |  | LE0 | KN26_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_ES | KN26_ES (非取樣點) | FEEDER | S76/11/KN26/ES |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN27 | KN27_ES |  | LE0 | KN27_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_ES | KN27_ES (非取樣點) | FEEDER | S76/11/KN27/ES |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN28 | KN28_ES |  | LE0 | KN28_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_ES | KN28_ES (非取樣點) | FEEDER | S76/11/KN28/ES |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN29 | KN29_ES |  | LE0 | KN29_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_ES | KN29_ES (非取樣點) | FEEDER | S76/11/KN29/ES |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN30 | KN30_ES |  | LE0 | KN30_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_ES | KN30_ES (非取樣點) | FEEDER | S76/11/KN30/ES |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN31 | KN31_DS |  | DS1 | KN31_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_DS | KN31_DS (非取樣點) | FEEDER | S76/11/KN31/DS |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN31 | KN31_ES |  | LE0 | KN31_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN31_ES | KN31_ES (非取樣點) | FEEDER | S76/11/KN31/ES |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN32 | KN32_DS |  | DS1 | KN32_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_DS | KN32_DS (非取樣點) | FEEDER | S76/11/KN32/DS |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN32 | KN32_ES |  | LE0 | KN32_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN32_ES | KN32_ES (非取樣點) | FEEDER | S76/11/KN32/ES |  |  |  |  | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN33 | KN33_DS |  | DS1 | KN33_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_DS | KN33_DS (非取樣點) | FEEDER | S76/11/KN33/DS |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN33 | KN33_ES |  | LE0 | KN33_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN33_ES | KN33_ES (非取樣點) | FEEDER | S76/11/KN33/ES |  |  |  |  | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN34 | KN34_DS |  | DS1 | KN34_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_DS | KN34_DS (非取樣點) | FEEDER | S76/11/KN34/DS |  |  |  |  | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN34 | KN34_ES |  | LE0 | KN34_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN34_ES | KN34_ES (非取樣點) | FEEDER | S76/11/KN34/ES |  |  |  |  | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN35 | KN35_DS |  | DS1 | KN35_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_DS | KN35_DS (非取樣點) | FEEDER | S76/11/KN35/DS |  |  |  |  | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN35 | KN35_ES |  | LE0 | KN35_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN35_ES | KN35_ES (非取樣點) | FEEDER | S76/11/KN35/ES |  |  |  |  | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN36 | KN36_DS |  | DS1 | KN36_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_DS | KN36_DS (非取樣點) | FEEDER | S76/11/KN36/DS |  |  |  |  | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN36 | KN36_ES |  | LE0 | KN36_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN36_ES | KN36_ES (非取樣點) | FEEDER | S76/11/KN36/ES |  |  |  |  | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN37 | KN37_DS |  | DS1 | KN37_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_DS | KN37_DS (非取樣點) | FEEDER | S76/11/KN37/DS |  |  |  |  | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN37 | KN37_ES |  | LE0 | KN37_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN37_ES | KN37_ES (非取樣點) | FEEDER | S76/11/KN37/ES |  |  |  |  | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN38 | KN38_DS |  | DS1 | KN38_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_DS | KN38_DS (非取樣點) | FEEDER | S76/11/KN38/DS |  |  |  |  | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN38 | KN38_ES |  | LE0 | KN38_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN38_ES | KN38_ES (非取樣點) | FEEDER | S76/11/KN38/ES |  |  |  |  | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN39 | KN39_DS |  | DS1 | KN39_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_DS | KN39_DS (非取樣點) | FEEDER | S76/11/KN39/DS |  |  |  |  | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN39 | KN39_ES |  | LE0 | KN39_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN39_ES | KN39_ES (非取樣點) | FEEDER | S76/11/KN39/ES |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN40 | KN40_DS |  | DS1 | KN40_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_DS | KN40_DS (非取樣點) | FEEDER | S76/11/KN40/DS |  |  |  |  | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN40 | KN40_ES |  | LE0 | KN40_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN40_ES | KN40_ES (非取樣點) | FEEDER | S76/11/KN40/ES |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN41 | KN41_DS |  | DS1 | KN41_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_DS | KN41_DS (非取樣點) | FEEDER | S76/11/KN41/DS |  |  |  |  | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN41 | KN41_ES |  | LE0 | KN41_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN41_ES | KN41_ES (非取樣點) | FEEDER | S76/11/KN41/ES |  |  |  |  | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN42 | KN42_DS |  | DS1 | KN42_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_DS | KN42_DS (非取樣點) | FEEDER | S76/11/KN42/DS |  |  |  |  | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN42 | KN42_ES |  | LE0 | KN42_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN42_ES | KN42_ES (非取樣點) | FEEDER | S76/11/KN42/ES |  |  |  |  | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN43 | KN43_DS |  | DS1 | KN43_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_DS | KN43_DS (非取樣點) | FEEDER | S76/11/KN43/DS |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN43 | KN43_ES |  | LE0 | KN43_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN43_ES | KN43_ES (非取樣點) | FEEDER | S76/11/KN43/ES |  |  |  |  | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN44 | KN44_DS |  | DS1 | KN44_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_DS | KN44_DS (非取樣點) | FEEDER | S76/11/KN44/DS |  |  |  |  | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN44 | KN44_ES |  | LE0 | KN44_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN44_ES | KN44_ES (非取樣點) | FEEDER | S76/11/KN44/ES |  |  |  |  | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN45 | KN45_DS |  | DS1 | KN45_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_DS | KN45_DS (非取樣點) | FEEDER | S76/11/KN45/DS |  |  |  |  | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN45 | KN45_ES |  | LE0 | KN45_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN45_ES | KN45_ES (非取樣點) | FEEDER | S76/11/KN45/ES |  |  |  |  | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | TIE1 | #2B-#1 |  | DS1 | TIE1_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE1_DS | #2B-#1 TIE_DS (非取樣點) | TIE | S76/11/TIE1/D1 |  |  |  |  | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | TIE2 | #3-#2A |  | DS1 | TIE2_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE2_DS | #3-#2A TIE_DS (非取樣點) | TIE | S76/11/TIE2/D1 |  |  |  |  | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | TIE3 | TIE3_DS |  | DS1 | TIE3_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE3_DS | TIE3_DS (非取樣點) | TIE | S76/11/TIE3/DS |  |  |  |  | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | TIE4 | #4-#5 |  | DS1 | TIE4_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE4_DS | #4-#5 TIE_DS (非取樣點) | TIE | S76/11/TIE4/D1 |  |  |  |  | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | TIE5 | TIE5_DS |  | DS1 | TIE5_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE5_DS | TIE5_DS (非取樣點) | TIE | S76/11/TIE5/DS |  |  |  |  | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 1M | 1M_DS |  | DS1 | 1M_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.1M_DS | 1M_DS (非取樣點) | DTR | S76/11/M1/DS |  |  |  |  | 802 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 1M | 1M_ES |  | M0 | 1M_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.1M_ES | 1M_ES (非取樣點) | DTR | S76/11/M1/ES |  |  |  |  | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 3M | 3M_DS |  | DS1 | 3M_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.3M_DS | 3M_DS (非取樣點) | DTR | S76/11/M3/DS |  |  |  |  | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 3M | 3M_ES |  | M0 | 3M_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.3M_ES | 3M_ES (非取樣點) | DTR | S76/11/M3/ES |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 4M | 4M_DS |  | DS1 | 4M_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.4M_DS | 4M_DS (非取樣點) | DTR | S76/11/M4/DS |  |  |  |  | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 4M | 4M_ES |  | M0 | 4M_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.4M_ES | 4M_ES (非取樣點) | DTR | S76/11/M4/ES |  |  |  |  | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 5M | 5M_DS |  | DS1 | 5M_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.5M_DS | 5M_DS (非取樣點) | DTR | S76/11/M5/DS |  |  |  |  | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 5M | 5M_ES |  | M0 | 5M_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.5M_ES | 5M_ES (非取樣點) | DTR | S76/11/M5/ES |  |  |  |  | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 210SCES | 210SCES |  | 210SCES | 210SCES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.210SCES | 210SCES (非取樣點) | SC | S76/11/210/ES |  |  |  |  | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 220SCES | 220SCES |  | 220SCES | 220SCES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.220SCES | 220SCES (非取樣點) | SC | S76/11/220/ES |  |  |  |  | 811 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 230SCES | 230SCES |  | 230SCES | 230SCES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.230SCES | 230SCES (非取樣點) | SC | S76/11/230/ES |  |  |  |  | 812 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.230_DS | 230_DS (非取樣點) | SC | S76/11/230/DS |  |  |  |  | 813 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 240SCES | 240SCES |  | 240SCES | 240SCES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.240SCES | 240SCES (非取樣點) | SC | S76/11/240/ES |  |  |  |  | 814 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.240_DS | 240_DS (非取樣點) | SC | S76/11/240/DS |  |  |  |  | 815 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 250SCES | 250SCES |  | 250SCES | 250SCES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.250SCES | 250SCES (非取樣點) | SC | S76/11/250/ES |  |  |  |  | 816 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.250_DS | 250_DS (非取樣點) | SC | S76/11/250/DS |  |  |  |  | 817 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 佳一SS.69B1E | 69B1E (非取樣點) | BUS | S76/69/1BUS/BE1 |  |  |  |  | 818 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 819 | NotelDIPoint | [38 empty] | START/STOP | STOP
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | LE0 | 650LE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.650LE | 650LE (非取樣點) | LINE69 | S76/69/650/LE0 |  |  |  |  | 820 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | LE0 | 730LE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.730LE | 730LE (非取樣點) | LINE69 | S76/69/730/LE0 |  |  |  |  | 821 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN01 | KN01_DS |  | DS1 | KN01_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_DS | KN01_DS (非取樣點) | FEEDER | S76/11/KN01/DS |  |  |  |  | 822 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN01 | KN01_ES |  | LE0 | KN01_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN01_ES | KN01_ES (非取樣點) | FEEDER | S76/11/KN01/ES |  |  |  |  | 823 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN21 | KN21_DS |  | DS1 | KN21_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN21_DS | KN21_DS (非取樣點) | FEEDER | S76/11/KN21/DS |  |  |  |  | 824 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN22 | KN22_DS |  | DS1 | KN22_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN22_DS | KN22_DS (非取樣點) | FEEDER | S76/11/KN22/DS |  |  |  |  | 825 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN23 | KN23_DS |  | DS1 | KN23_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN23_DS | KN23_DS (非取樣點) | FEEDER | S76/11/KN23/DS |  |  |  |  | 826 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN24 | KN24_DS |  | DS1 | KN24_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN24_DS | KN24_DS (非取樣點) | FEEDER | S76/11/KN24/DS |  |  |  |  | 827 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN25 | KN25_DS |  | DS1 | KN25_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_DS | KN25_DS (非取樣點) | FEEDER | S76/11/KN25/DS |  |  |  |  | 828 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN25 | KN25_ES |  | LE0 | KN25_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN25_ES | KN25_ES (非取樣點) | FEEDER | S76/11/KN25/ES |  |  |  |  | 829 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 1BR | 1BR_DS |  | DS1 | 1BR_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.1BR_DS | 1BR_DS (非取樣點) | TIE | S76/11/1BR/DS |  |  |  |  | 830 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.210_DS | 210_DS (非取樣點) | SC | S76/11/210/DS |  |  |  |  | 831 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 1BR | 1BR |  | BR0 | 1BR_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.1BR_ES | 1BR ES(非取樣點) | OTHER | S76/11/1BR/ES |  |  |  |  | 832 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 佳一SS.601E | 601E (非取樣點) | TIE | S76/69/600/E1 |  |  |  |  | 833 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 佳一SS.602E | 602E (非取樣點) | TIE | S76/69/600/E2 |  |  |  |  | 834 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.750TE | 750TE (非取樣點) | DTR | S76/69/750/TE0 |  |  |  |  | 835 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.750BE | 750BE (非取樣點) | DTR | S76/69/750/BE0 |  |  |  |  | 836 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 佳一SS.69B2E | 69B2E (非取樣點) | BUS | S76/69/2BUS/BE2 |  |  |  |  | 837 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN02 | KN02_DS |  | DS1 | KN02_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_DS | KN02_DS (非取樣點) | FEEDER | S76/11/KN02/DS |  |  |  |  | 838 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN02 | KN02_ES |  | LE0 | KN02_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN02_ES | KN02_ES (非取樣點) | FEEDER | S76/11/KN02/ES |  |  |  |  | 839 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | KN26 | KN26_DS |  | DS1 | KN26_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN26_DS | KN26_DS (非取樣點) | FEEDER | S76/11/KN26/DS |  |  |  |  | 840 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN27 | KN27_DS |  | DS1 | KN27_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN27_DS | KN27_DS (非取樣點) | FEEDER | S76/11/KN27/DS |  |  |  |  | 841 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN28 | KN28_DS |  | DS1 | KN28_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN28_DS | KN28_DS (非取樣點) | FEEDER | S76/11/KN28/DS |  |  |  |  | 842 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN29 | KN29_DS |  | DS1 | KN29_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN29_DS | KN29_DS (非取樣點) | FEEDER | S76/11/KN29/DS |  |  |  |  | 843 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | KN30 | KN30_DS |  | DS1 | KN30_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.KN30_DS | KN30_DS (非取樣點) | FEEDER | S76/11/KN30/DS |  |  |  |  | 844 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2BR | 2BR_DS |  | DS1 | 2BR_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.2BR_DS | 2BR_DS (非取樣點) | TIE | S76/11/2BR/DS |  |  |  |  | 845 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.391 | 391 (非取樣點) | OTHER | S76/11/390/DS |  |  |  |  | 846 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.391E | 391E (非取樣點) | OTHER | S76/11/390/ES |  |  |  |  | 847 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 2MA | 2MA_DS |  | DS1 | 2MA_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MA_DS | 2MA_DS (非取樣點) | DTR | S76/11/M2A/DS |  |  |  |  | 848 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2MB | 2MB_DS |  | DS1 | 2MB_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MB_DS | 2MB_DS (非取樣點) | DTR | S76/11/M2B/DS |  |  |  |  | 849 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2MA | 2MA_ES |  | MA0 | 2MA_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MA_ES | 2MA_ES (非取樣點) | DTR | S76/11/M2A/ES |  |  |  |  | 850 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 2MB | 2MB_ES |  | MB0 | 2MB_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.2MB_ES | 2MB_ES (非取樣點) | DTR | S76/11/M2B/ES |  |  |  |  | 851 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.220_DS | 220_DS (非取樣點) | SC | S76/11/220/DS |  |  |  |  | 852 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S76 | 佳里一SS | 0 |  | 2BR | 2BR |  | BR0 | 2BR_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.2BR_ES | 2BR ES(非取樣點) | OTHER | S76/11/2BR/ES |  |  |  |  | 853 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | TIE1 | #2B-#1 |  | LE0 | TIE1_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.TIE1_ES | #2B-#1 TIE ES(非取樣點) | OTHER | S76/11/TIE1/E1 |  |  |  |  | 854 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.810BE | 810BE (非取樣點) | SC | S76/69/810/BE0 |  |  |  |  | 855 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 810CE | 810CE |  | 810CE | 810CE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.810CE | 810CE (非取樣點) | SC | S76/69/810/ES |  |  |  |  | 856 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 620 | 學甲佳里二路(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.620BE | 620BE (非取樣點) | LINE69 | S76/69/620/BE0 |  |  |  |  | 857 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 730 | 學甲佳里一路(730) |  | BE0 | 730BE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.730BE | 730BE (非取樣點) | LINE69 | S76/69/730/BE0 |  |  |  |  | 858 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 1 | #1 |  | BE | #1_BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.#1_BE | #1 BE(非取樣點) | OTHER | S76/11/1BUS/BE0 |  |  |  |  | 859 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2A_BE | #2A BE(非取樣點) | OTHER | S76/11/2ABUS/BE0 |  |  |  |  | 860 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.#2B_BE | #2B BE(非取樣點) | OTHER | S76/11/2BBUS/BE0 |  |  |  |  | 861 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | TE0 | 790TE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.790TE | 790TE (非取樣點) | DTR | S76/69/790/TE0 |  |  |  |  | 862 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 790 | #5MTR(790) |  | BE0 | 790BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.790BE | 790BE (非取樣點) | DTR | S76/69/790/BE0 |  |  |  |  | 863 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.780TE | 780TE (非取樣點) | DTR | S76/69/780/TE0 |  |  |  |  | 864 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.780BE | 780BE (非取樣點) | DTR | S76/69/780/BE0 |  |  |  |  | 865 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.760TE | 760TE (非取樣點) | DTR | S76/69/760/TE0 |  |  |  |  | 866 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.760BE | 760BE (非取樣點) | DTR | S76/69/760/BE0 |  |  |  |  | 867 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 650 | 佳里麻豆線(650) |  | BE0 | 650BE | [24 empty] | ADCS_N | [8 empty] | 佳一SS.650BE | 650BE (非取樣點) | LINE69 | S76/69/650/BE0 |  |  |  |  | 868 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.770TE | 770TE (非取樣點) | DTR | S76/69/770/TE0 |  |  |  |  | 869 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S76 | 佳里一SS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | DDCS4_2 | [8 empty] | 佳一SS.770BE | 770BE (非取樣點) | DTR | S76/69/770/BE0 |  |  |  |  | 870 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo