## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S77 | 佳里二SS | 11 | 11kV | 6BUS | #6BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0024 |  |  | 1-98 |  |  | #6 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aga | B2/S77_D1 | [8 empty] | 佳二SS.11KV#6BUS_KV | 11KV #6BUS KV | BUS |  |  |  |  | CDC | 2 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S77 | 佳里二SS | 11 | 11kV | 7BUS | #7BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0060 |  |  | 1-BC |  |  | #7 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aha | B2/S77_D1 | [8 empty] | 佳二SS.11KV#7BUS_KV | 11KV #7BUS KV | BUS |  |  |  |  | CDC | 3 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 佳20線 (F1) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳20線KVAR | 11KV佳20線 KVAR | FEEDER |  |  |  |  | CDC | 4 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 佳20線 (F1) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳20線A1 | 11KV佳20線 R相AMP | FEEDER |  |  |  |  | CDC | 5 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 佳20線 (F1) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳20線A2 | 11KV佳20線 S相AMP | FEEDER |  |  |  |  | CDC | 6 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 佳20線 (F1) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳20線A3 | 11KV佳20線 T相AMP | FEEDER |  |  |  |  | CDC | 7 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 佳20線 (F1) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳20線A0 | 11KV佳20線 N相AMP | FEEDER |  |  |  |  | CDC | 8 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0000 |  |  | 1-40 |  |  | 佳20線 (F1) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 9 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 佳16線 (F5) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳16線KVAR | 11KV佳16線 KVAR | FEEDER |  |  |  |  | CDC | 10 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 佳16線 (F5) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳16線A1 | 11KV佳16線 R相AMP | FEEDER |  |  |  |  | CDC | 11 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 佳16線 (F5) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳16線A2 | 11KV佳16線 S相AMP | FEEDER |  |  |  |  | CDC | 12 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 佳16線 (F5) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳16線A3 | 11KV佳16線 T相AMP | FEEDER |  |  |  |  | CDC | 13 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 佳16線 (F5) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳16線A0 | 11KV佳16線 N相AMP | FEEDER |  |  |  |  | CDC | 14 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0004 |  |  | 1-44 |  |  | 佳16線 (F5) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 15 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 佳14線 (F9) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳14線KVAR | 11KV佳14線 KVAR | FEEDER |  |  |  |  | CDC | 16 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 佳14線 (F9) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳14線A1 | 11KV佳14線 R相AMP | FEEDER |  |  |  |  | CDC | 17 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 佳14線 (F9) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳14線A2 | 11KV佳14線 S相AMP | FEEDER |  |  |  |  | CDC | 18 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 佳14線 (F9) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳14線A3 | 11KV佳14線 T相AMP | FEEDER |  |  |  |  | CDC | 19 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 佳14線 (F9) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳14線A0 | 11KV佳14線 N相AMP | FEEDER |  |  |  |  | CDC | 20 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0008 |  |  | 1-48 |  |  | 佳14線 (F9) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 21 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | KVAR |  | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 佳15線 (F10) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳15線KVAR | 11KV佳15線 KVAR | FEEDER |  |  |  |  | CDC | 22 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | I_R |  | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 佳15線 (F10) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳15線A1 | 11KV佳15線 R相AMP | FEEDER |  |  |  |  | CDC | 23 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | I_S |  | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 佳15線 (F10) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳15線A2 | 11KV佳15線 S相AMP | FEEDER |  |  |  |  | CDC | 24 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | I_T |  | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 佳15線 (F10) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳15線A3 | 11KV佳15線 T相AMP | FEEDER |  |  |  |  | CDC | 25 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | I_N |  | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 佳15線 (F10) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳15線A0 | 11KV佳15線 N相AMP | FEEDER |  |  |  |  | CDC | 26 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | kWh |  | B3 | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0009 |  |  | 1-49 |  |  | 佳15線 (F10) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 27 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 佳20線 (F1) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN20_PHA | 11KV佳20線(KN20) 相間RY | FEEDER |  |  |  |  | CDC | 28 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | 佳20線 (F1) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN20_GDA | 11KV佳20線(KN20) 接地RY | FEEDER |  |  |  |  | CDC | 29 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0311 |  | 0060 | 1-33-07 |  | 1-3C | 佳20線 (F1) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN20_79UL | 11KV佳20線(KN20) 79RY U/L | FEEDER |  |  |  |  | CDC | 30 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0352 |  | 0112 | 1-36-00 |  | 1-70 | 佳20線 (F1) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN20_ADJ | 11KV佳20線(KN20) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 31 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | 佳農線 (F2) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN19_PHA | 11KV佳農線(KN19) 相間RY | FEEDER |  |  |  |  | CDC | 32 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 佳農線 (F2) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN19_GDA | 11KV佳農線(KN19) 接地RY | FEEDER |  |  |  |  | CDC | 33 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0312 |  | 0061 | 1-33-08 |  | 1-3D | 佳農線 (F2) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN19_79UL | 11KV佳農線(KN19) 79RY U/L | FEEDER |  |  |  |  | CDC | 34 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0353 |  | 0113 | 1-36-01 |  | 1-71 | 佳農線 (F2) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN19_ADJ | 11KV佳農線(KN19) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 35 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 佳頂線 (F3) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN18_PHA | 11KV佳頂線(KN18) 相間RY | FEEDER |  |  |  |  | CDC | 36 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | 佳頂線 (F3) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN18_GDA | 11KV佳頂線(KN18) 接地RY | FEEDER |  |  |  |  | CDC | 37 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0313 |  | 0062 | 1-33-09 |  | 1-3E | 佳頂線 (F3) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN18_79UL | 11KV佳頂線(KN18) 79RY U/L | FEEDER |  |  |  |  | CDC | 38 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0354 |  | 0114 | 1-36-02 |  | 1-72 | 佳頂線 (F3) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN18_ADJ | 11KV佳頂線(KN18) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 39 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | 佳坪線 (F4) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN17_PHA | 11KV佳坪線(KN17) 相間RY | FEEDER |  |  |  |  | CDC | 40 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | 佳坪線 (F4) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN17_GDA | 11KV佳坪線(KN17) 接地RY | FEEDER |  |  |  |  | CDC | 41 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0314 |  | 0063 | 1-33-10 |  | 1-3F | 佳坪線 (F4) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN17_79UL | 11KV佳坪線(KN17) 79RY U/L | FEEDER |  |  |  |  | CDC | 42 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0355 |  | 0115 | 1-36-03 |  | 1-73 | 佳坪線 (F4) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN17_ADJ | 11KV佳坪線(KN17) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 43 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0113 |  |  | 1-0E-01 |  |  | 佳16線 (F5) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN16_PHA | 11KV佳16線(KN16) 相間RY | FEEDER |  |  |  |  | CDC | 44 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | 佳16線 (F5) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN16_GDA | 11KV佳16線(KN16) 接地RY | FEEDER |  |  |  |  | CDC | 45 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0315 |  | 0064 | 1-33-11 |  | 1-40 | 佳16線 (F5) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN16_79UL | 11KV佳16線(KN16) 79RY U/L | FEEDER |  |  |  |  | CDC | 46 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0356 |  | 0116 | 1-36-04 |  | 1-74 | 佳16線 (F5) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN16_ADJ | 11KV佳16線(KN16) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 47 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 佳安線 (F6) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN11_PHA | 11KV佳安線(KN11) 相間RY | FEEDER |  |  |  |  | CDC | 48 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 佳安線 (F6) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN11_GDA | 11KV佳安線(KN11) 接地RY | FEEDER |  |  |  |  | CDC | 49 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0081 | 1-34-07 |  | 1-51 | 佳安線 (F6) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN11_79UL | 11KV佳安線(KN11) 79RY U/L | FEEDER |  |  |  |  | CDC | 50 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0357 |  | 0117 | 1-36-05 |  | 1-75 | 佳安線 (F6) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN11_ADJ | 11KV佳安線(KN11) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 51 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 佳華線 (F7) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN12_PHA | 11KV佳華線(KN12) 相間RY | FEEDER |  |  |  |  | CDC | 52 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 佳華線 (F7) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN12_GDA | 11KV佳華線(KN12) 接地RY | FEEDER |  |  |  |  | CDC | 53 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0082 | 1-34-08 |  | 1-52 | 佳華線 (F7) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN12_79UL | 11KV佳華線(KN12) 79RY U/L | FEEDER |  |  |  |  | CDC | 54 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0358 |  | 0118 | 1-36-06 |  | 1-76 | 佳華線 (F7) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN12_ADJ | 11KV佳華線(KN12) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 55 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 佳洲線 (F8) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN13_PHA | 11KV佳洲線(KN13) 相間RY | FEEDER |  |  |  |  | CDC | 56 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | 佳洲線 (F8) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN13_GDA | 11KV佳洲線(KN13) 接地RY | FEEDER |  |  |  |  | CDC | 57 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0083 | 1-34-09 |  | 1-53 | 佳洲線 (F8) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN13_79UL | 11KV佳洲線(KN13) 79RY U/L | FEEDER |  |  |  |  | CDC | 58 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0359 |  | 0119 | 1-36-07 |  | 1-77 | 佳洲線 (F8) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN13_ADJ | 11KV佳洲線(KN13) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 59 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 佳14線 (F9) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN14_PHA | 11KV佳14線(KN14) 相間RY | FEEDER |  |  |  |  | CDC | 60 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | 佳14線 (F9) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN14_GDA | 11KV佳14線(KN14) 接地RY | FEEDER |  |  |  |  | CDC | 61 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0084 | 1-34-10 |  | 1-54 | 佳14線 (F9) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN14_79UL | 11KV佳14線(KN14) 79RY U/L | FEEDER |  |  |  |  | CDC | 62 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0360 |  | 0120 | 1-36-08 |  | 1-78 | 佳14線 (F9) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN14_ADJ | 11KV佳14線(KN14) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 63 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 佳15線 (F10) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN15_PHA | 11KV佳15線(KN15) 相間RY | FEEDER |  |  |  |  | CDC | 64 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 佳15線 (F10) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN15_GDA | 11KV佳15線(KN15) 接地RY | FEEDER |  |  |  |  | CDC | 65 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0085 | 1-34-11 |  | 1-55 | 佳15線 (F10) 79RY U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN15_79UL | 11KV佳15線(KN15) 79RY U/L | FEEDER |  |  |  |  | CDC | 66 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | ADJ |  | Element | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0361 |  | 0121 | 1-36-09 |  | 1-79 | 佳15線 (F10) LCO ADJ U/L |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN15_ADJ | 11KV佳15線(KN15) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 67 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/7BUS | L/KN20/T1 |  |  | 0096 |  | 0052 | 1-0C-00 |  | 1-34 | 佳20線 (F1) CB |  |  |  | ahab | B2/S77_D1 | [8 empty] | 佳二SS.KN20_CB | KN20(11KV佳20線) CB | FEEDER |  |  |  |  | CDC | 68 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN20_DS | KN20_DS (非取樣點) | FEEDER | [5 empty] | 69 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | ES | KN20_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN20_ES | KN20_ES (非取樣點) | FEEDER | [5 empty] | 70 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/7BUS | L/KN19/T1 |  |  | 0097 |  | 0053 | 1-0C-01 |  | 1-35 | 佳農線 (F2) CB |  |  |  | ahbb | B2/S77_D1 | [8 empty] | 佳二SS.KN19_CB | KN19(11KV佳農線) CB | FEEDER |  |  |  |  | CDC | 71 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN19_DS | KN19_DS (非取樣點) | FEEDER | [5 empty] | 72 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | ES | KN19_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN19_ES | KN19_ES (非取樣點) | FEEDER | [5 empty] | 73 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/7BUS | L/KN18/T1 |  |  | 0098 |  | 0054 | 1-0C-02 |  | 1-36 | 佳頂線 (F3) CB |  |  |  | ahdb | B2/S77_D1 | [8 empty] | 佳二SS.KN18_CB | KN18(11KV佳頂線) CB | FEEDER |  |  |  |  | CDC | 74 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN18_DS | KN18_DS (非取樣點) | FEEDER | [5 empty] | 75 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | ES | KN18_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN18_ES | KN18_ES (非取樣點) | FEEDER | [5 empty] | 76 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/7BUS | L/KN17/T1 |  |  | 0099 |  | 0055 | 1-0C-03 |  | 1-37 | 佳坪線 (F4) CB |  |  |  | aheb | B2/S77_D1 | [8 empty] | 佳二SS.KN17_CB | KN17(11KV佳坪線) CB | FEEDER |  |  |  |  | CDC | 77 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN17_DS | KN17_DS (非取樣點) | FEEDER | [5 empty] | 78 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | ES | KN17_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN17_ES | KN17_ES (非取樣點) | FEEDER | [5 empty] | 79 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/7BUS | L/KN16/T1 |  |  | 0100 |  | 0056 | 1-0C-04 |  | 1-38 | 佳16線 (F5) CB |  |  |  | ahfb | B2/S77_D1 | [8 empty] | 佳二SS.KN16_CB | KN16(11KV佳16線) CB | FEEDER |  |  |  |  | CDC | 80 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN16_DS | KN16_DS (非取樣點) | FEEDER | [5 empty] | 81 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | ES | KN16_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN16_ES | KN16_ES (非取樣點) | FEEDER | [5 empty] | 82 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KN11/T1 |  |  | 0118 |  | 0073 | 1-0E-06 |  | 1-49 | 佳安線 (F6) CB |  |  |  | agbb | B2/S77_D1 | [8 empty] | 佳二SS.KN11_CB | KN11(11KV佳安線) CB | FEEDER |  |  |  |  | CDC | 83 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN11_DS | KN11_DS (非取樣點) | FEEDER | [5 empty] | 84 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | ES | KN11_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN11_ES | KN11_ES (非取樣點) | FEEDER | [5 empty] | 85 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KN12/T1 |  |  | 0119 |  | 0074 | 1-0E-07 |  | 1-4A | 佳華線 (F7) CB |  |  |  | agcb | B2/S77_D1 | [8 empty] | 佳二SS.KN12_CB | KN12(11KV佳華線) CB | FEEDER |  |  |  |  | CDC | 86 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN12_DS | KN12_DS (非取樣點) | FEEDER | [5 empty] | 87 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | ES | KN12_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN12_ES | KN12_ES (非取樣點) | FEEDER | [5 empty] | 88 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KN13/T1 |  |  | 0120 |  | 0075 | 1-0F-00 |  | 1-4B | 佳洲線 (F8) CB |  |  |  | ageb | B2/S77_D1 | [8 empty] | 佳二SS.KN13_CB | KN13(11KV佳洲線) CB | FEEDER |  |  |  |  | CDC | 89 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN13_DS | KN13_DS (非取樣點) | FEEDER | [5 empty] | 90 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | ES | KN13_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN13_ES | KN13_ES (非取樣點) | FEEDER | [5 empty] | 91 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KN14/T1 |  |  | 0121 |  | 0076 | 1-0F-01 |  | 1-4C | 佳14線 (F9) CB |  |  |  | agfb | B2/S77_D1 | [8 empty] | 佳二SS.KN14_CB | KN14(11KV佳14線) CB | FEEDER |  |  |  |  | CDC | 92 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN14_DS | KN14_DS (非取樣點) | FEEDER | [5 empty] | 93 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | ES | KN14_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN14_ES | KN14_ES (非取樣點) | FEEDER | [5 empty] | 94 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | L/KN15/T1 |  |  | 0122 |  | 0077 | 1-0F-02 |  | 1-4D | 佳15線 (F10) CB |  |  |  | aggb | B2/S77_D1 | [8 empty] | 佳二SS.KN15_CB | KN15(11KV佳15線) CB | FEEDER |  |  |  |  | CDC | 95 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN15_DS | KN15_DS (非取樣點) | FEEDER | [5 empty] | 96 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | ES | KN15_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.KN15_ES | KN15_ES (非取樣點) | FEEDER | [5 empty] | 97 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | TIE6 | TIE(TIE6) |  | I_R | #7-#6 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | #6-#7 TIE R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.11KV_TIE6_A1 | 11KV #7-#6 TIE R相AMP | TIE |  |  |  |  | CDC | 98 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | TIE6 | TIE(TIE6) |  | I_S | #7-#6 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | #6-#7 TIE S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.11KV_TIE6_A2 | 11KV #7-#6 TIE S相AMP | TIE |  |  |  |  | CDC | 99 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | TIE6 | TIE(TIE6) |  | I_T | #7-#6 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | #6-#7 TIE T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.11KV_TIE6_A3 | 11KV #7-#6 TIE T相AMP | TIE |  |  |  |  | CDC | 100 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #6 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#6MTR_MW | #6MTR二次側 MW | DTR |  |  |  |  | CDC | 101 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #6 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#6MTR_MVAR | #6MTR二次側 MVAR | DTR |  |  |  |  | CDC | 102 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #6 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#6MTR_A1 | #6MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 103 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #6 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#6MTR_A2 | #6MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 104 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #6 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#6MTR_A3 | #6MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 105 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #7 TR 瓦 |  |  | MW_-36_36(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#7MTR_MW | #7MTR二次側 MW | DTR |  |  |  |  | CDC | 106 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #7 TR 乏 |  |  | MVAR_-36_36(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#7MTR_MVAR | #7MTR二次側 MVAR | DTR |  |  |  |  | CDC | 107 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #7 TR R相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#7MTR_A1 | #7MTR二次側 R相AMP | DTR |  |  |  |  | CDC | 108 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #7 TR S相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#7MTR_A2 | #7MTR二次側 S相AMP | DTR |  |  |  |  | CDC | 109 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #7 TR T相電流 |  |  | A_-2000_2000(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.#7MTR_A3 | #7MTR二次側 T相AMP | DTR |  |  |  |  | CDC | 110 | AI_DTR(1) |  |  |  | AI | [5 empty] | LG_1205 | 1084.5 | 1205 | 1325.5 | 1506.2 | 1 | -1084.5 | -1205 | -1325.5 | -1506.2 | 1 | 0.01 | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #6 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_OIL | #6MTR 油溫 | DTR |  |  |  |  | CDC | 111 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #6 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_COIL | #6MTR 線溫 | DTR |  |  |  |  | CDC | 112 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0057 | 1-9B |  | 1-39 | #6 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_TAP | #6MTR OLTC TAP | DTR |  |  |  |  | CDC | 113 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0015 |  |  | 1-4F |  |  | #6 TR MWH(+) |  |  |  |  | B1/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 114 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | MVARH_P |  | Element | [12 empty] | 0016 |  |  | 1-50 |  |  | #6 TR MVARH(+) |  |  |  |  | B1/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 115 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | #7 TR 油溫 |  |  | OIL_-120_120(-2000_2000) |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_OIL | #7MTR 油溫 | DTR |  |  |  |  | CDC | 116 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | #7 TR 線溫 |  |  | COIL_-120_120(-2000_2000) |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_COIL | #7MTR 線溫 | DTR |  |  |  |  | CDC | 117 | AI_DTR(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0063 |  | 0078 | 1-BF |  | 1-4E | #7 TAP 位置 |  |  | TAP_-4.5_12.5(0_2000) |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_TAP | #7MTR OLTC TAP | DTR |  |  |  |  | CDC | 118 | AI_DTR(2) |  |  |  | AI | [5 empty] | TAP12_4 | 11 | 12 | 13 | 14 | 0 | -3 | -4 | -5 | -6 | 0.1 |  | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | MWh |  |  | cv60mAc | MWh RawCount |  | Y |  | ACC | [6 empty] | 0018 |  |  | 1-52 |  |  | #7 TR MWH(+) |  |  |  |  | B1/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 119 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | MVARH_P |  | Element | [12 empty] | 0019 |  |  | 1-53 |  |  | #7 TR MVARH(+) |  |  |  |  | B1/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 120 | AI_DTR(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/6MTR |  | 0001 |  | 0048 | 1-00-01 |  | 1-30 | #6TR 一次 (860) CB |  |  |  | aakb | B3/S77_D1 | [8 empty] | 佳二SS.860_CB | 860(#6MTR) CB | DTR |  |  |  |  | CDC | 121 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1BUS | B/2BUS | T/7MTR |  | 0010 |  | 0068 | 1-01-02 |  | 1-44 | #7TR 一次 (870) CB |  |  |  | aalb | B3/S77_D1 | [8 empty] | 佳二SS.870_CB | 870(#7MTR) CB | DTR |  |  |  |  | CDC | 122 | DI_DTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | T/6MTR |  |  | 0002 |  | 0049 | 1-00-02 |  | 1-31 | #6TR 二次 (#6MT) CB |  |  |  | agda | B2/S77_D1 | [8 empty] | 佳二SS.6M_CB | 6M(#6MTR) CB | DTR |  |  |  |  | CDC | 123 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/7BUS | T/7MTR |  |  | 0011 |  | 0069 | 1-01-03 |  | 1-45 | #7TR 二次 (#7MT) CB |  |  |  | ahca | B2/S77_D1 | [8 empty] | 佳二SS.7M_CB | 7M(#7MTR) CB | DTR |  |  |  |  | CDC | 124 | DI_DTR(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | #6TR 一次 (860) 51 RY |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.#6MTR_51A | #6MTR 51RY | DTR |  |  |  |  | CDC | 125 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | #6TR 一次 (860) 51N RY |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.#6MTR_51NA | #6MTR 51N RY | DTR |  |  |  |  | CDC | 126 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | #6TR 51Z RY |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_51ZA | #6MTR 51Z RY | DTR |  |  |  |  | CDC | 127 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | #6TR 87 RY |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_87A | #6MTR 87RY | DTR |  |  |  |  | CDC | 128 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0307 |  |  | 1-33-03 |  |  | #6TR 87 LS1S |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_87UL | #6MTR 87RY U/L | DTR |  |  |  |  | CDC | 129 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 81A |  | B2 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  | 0065 | 1-0C-06 |  | 1-41 | #6 BUS 81 RY |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_81A/S | #860 81RY A/S | DTR |  |  |  |  | CDC | 130 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | #7TR 一次 (870) 51 RY |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.#7MTR_51A | #7MTR 51RY | DTR |  |  |  |  | CDC | 131 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | 51NA |  | B2,B3 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | #7TR 一次 (870) 51N RY |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.#7MTR_51NA | #7MTR 51N RY | DTR |  |  |  |  | CDC | 132 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | #7TR 51Z RY |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_51ZA | #7MTR 51Z RY | DTR |  |  |  |  | CDC | 133 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | #7TR 87 RY |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_87A | #7MTR 87RY | DTR |  |  |  |  | CDC | 134 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-34-03 |  |  | #7TR 87 LS1S |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_87UL | #7MTR 87RY U/L | DTR |  |  |  |  | CDC | 135 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 81A |  | B2 | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  | 0086 | 1-0F-04 |  | 1-56 | #7 BUS 81 RY |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_81A/S | #7MTR 81RY A/S | DTR |  |  |  |  | CDC | 136 | DI_DTR(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | #6TR 二次 (#6MT) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.6M_51A | #6MTR二次側(6M) 51RY | DTR |  |  |  |  | CDC | 137 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0304 |  |  | 1-33-00 |  |  | #6TR 重故障 |  |  |  | a | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_TRA | #6MTR 重故障 | DTR |  |  |  |  | CDC | 138 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0305 |  |  | 1-33-01 |  |  | #6TR 輕故障 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_TRF | #6MTR 輕故障 | DTR |  |  |  |  | CDC | 139 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 1-33-04 |  |  | #6TR OLTC R/L |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_S/L | #6MTR OLTC S/L | DTR |  |  |  |  | CDC | 140 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0309 |  | 0058 | 1-33-05 |  | 1-3A | #6TR OLTC A/M |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_A/M | #6MTR OLTC A/M | DTR |  |  |  |  | CDC | 141 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | 51A |  | B3,Element | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #7TR 二次 (#7MT) 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.7M_51A | #7MTR二次側(7M) 51RY | DTR |  |  |  |  | CDC | 142 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0320 |  |  | 1-34-00 |  |  | #7TR 重故障 |  |  |  | a | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_TRA | #7MTR 重故障 | DTR |  |  |  |  | CDC | 143 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0321 |  |  | 1-34-01 |  |  | #7TR 輕故障 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_TRF | #7MTR 輕故障 | DTR |  |  |  |  | CDC | 144 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-34-04 |  |  | #7TR OLTC R/L |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_S/L | #7MTR OLTC S/L | DTR |  |  |  |  | CDC | 145 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0079 | 1-34-05 |  | 1-4F | #7TR OLTC A/M |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_A/M | #7MTR OLTC A/M | DTR |  |  |  |  | CDC | 146 | DI_DTR(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.6M_DS | 6M_DS (非取樣點) | DTR | [5 empty] | 147 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | ES | 6M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.6M_ES | 6M_ES (非取樣點) | DTR | [5 empty] | 148 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 96PA |  | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | #6TR 機械保護動作(96PA) |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_96PA | #6MTR 機械保護動作 | DTR |  |  |  |  | CDC | 149 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0306 |  |  | 1-33-02 |  |  | #6TR OLTC 遲滯 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_OLTC遲滯 | #6MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 150 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-33-12 |  |  | #6TR 冷卻電源故障 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_AC_FAULT | #6MTR AC電源失效 | DTR |  |  |  |  | CDC | 151 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.7M_DS | 7M_DS (非取樣點) | DTR | [5 empty] | 152 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | ES | 7M_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.7M_ES | 7M_ES (非取樣點) | DTR | [5 empty] | 153 | DI_DTR(6) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 96PA |  | Element | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | #7TR 機械保護動作(96PA) |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_96PA | #7MTR 機械保護動作 | DTR |  |  |  |  | CDC | 154 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | OLTC_DLY |  | Element | Status | OLTC遲滯 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-34-02 |  |  | #7TR OLTC 遲滯 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_OLTC遲滯 | #7MTR OLTC遲滯 | DTR |  |  |  |  | CDC | 155 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | AC_Fault |  |  | Status | AC電源失效 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-34-12 |  |  | #7TR 冷卻電源故障 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_AC_FAULT | #7MTR AC電源失效 | DTR |  |  |  |  | CDC | 156 | DI_DTR(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/6BUS | C/6SC |  |  | 0095 |  | 0051 | 1-0B-07 |  | 1-33 | #6 11KV SC CB |  |  |  | agab | B2/S77_D1 | [8 empty] | 佳二SS.260_CB | 260(11KV #6SC) CB | SC |  |  |  |  | CDC | 157 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0310 |  | 0059 | 1-33-06 |  | 1-3B | #6SC Q-CTL A/M |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.260_A/M | 11KV #6SC 乏控器 A/M | SC |  |  |  |  | CDC | 158 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | ES | 260_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 159 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/7BUS | C/7SC |  |  | 0117 |  | 0072 | 1-0E-05 |  | 1-48 | #7 11KV SC CB |  |  |  | ahgb | B2/S77_D1 | [8 empty] | 佳二SS.270_CB | 270(11KV #7SC) CB | SC |  |  |  |  | CDC | 160 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0326 |  | 0080 | 1-34-06 |  | 1-50 | #7SC Q-CTL A/M |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.270_A/M | 11KV #7SC 乏控器 A/M | SC |  |  |  |  | CDC | 161 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | ES | 270_ES(非取樣點) | DELETE | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.270_ES | 270_ES (非取樣點) | SC | [5 empty] | 162 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | #6SC 51,51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.260_SCA | 11KV #6SC 51,51N RY | SC |  |  |  |  | CDC | 163 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #6SC 27,59 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.260_UVA | 11KV #6SC 27RY(欠壓) | SC |  |  |  |  | CDC | 164 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #7SC 51,51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.270_SCA | 11KV #7SC 51,51N RY | SC |  |  |  |  | CDC | 165 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #7SC 27,59 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.270_UVA | 11KV #7SC 27RY(欠壓) | SC |  |  |  |  | CDC | 166 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 167 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | DS | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.270_DS | 270_DS (非取樣點) | SC | [5 empty] | 168 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | RTU | RTU |  | ADCL1 |  | B2 | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S77_D1 | [8 empty] | 佳二SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 169 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | RTU | RTU |  | ADCH1 |  | B2 | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S77_D1 | [8 empty] | 佳二SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 170 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | RTU | RTU |  | ADCL2 |  | B2 | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/S77_D1 | [8 empty] | 佳二SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 171 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | RTU | RTU |  | ADCH2 |  | B2 | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/S77_D1 | [8 empty] | 佳二SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 172 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0256 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  |  |  |  | ELEM/ALL | [8 empty] | 佳二SS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 173 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | RTU | RTU |  | RTU_R_L |  | B3,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0257 |  |  | 1-30-01 |  |  | L/R STATUS |  |  |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 174 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0258 |  |  | 1-30-02 |  |  | #1 充電機 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.直流充電機故障 | 直流充電機故障 | OTHER |  |  |  |  | CDC | 175 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0259 |  |  | 1-30-03 |  |  | #2 充電機 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.通訊充電機故障 | 通訊充電機故障 | OTHER |  |  |  |  | CDC | 176 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | 81A_RYFA | 低頻IED故障 |  | Status | 81RY RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 1-30-13 |  |  | 低頻電驛 IED故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.81RY_IED_FA | 低頻IED故障 | OTHER |  |  |  |  | CDC | 177 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0268 |  |  | 1-30-12 |  |  | Locate Empty |  |  |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 178 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | Door1 | 門禁保全 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0277 |  |  | 1-31-05 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 179 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | Water2 | 變電所高水位 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0278 |  |  | 1-31-06 |  |  | 11KV IED通訊故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.變電所高水位 | 變電所高水位 | OTHER |  |  |  |  | CDC | 180 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | ComPoint |  |  | IRFA | 11KV IED故障 | B2,B3,Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 1-31-07 |  |  | 11KV IED故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.11KV_IED_FA | 11KV IED故障 | OTHER |  |  |  |  | CDC | 181 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0274 |  |  | 1-31-02 |  |  | PowerMeter通訊故障(PMA) |  | Card6 CH115 |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.PM_CFA | PM通訊故障 | OTHER |  |  |  |  | CDC | 182 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | ComPoint |  |  | CFA | 69KV IED通訊故障 | B2,B3,Element | [12 empty] | 0275 |  |  | 1-31-03 |  |  | 69KV IED通訊故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER |  |  |  |  | CDC | 183 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | ComPoint |  |  | IRFA | 69KV IED故障 | B2,B3,Element | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 1-31-04 |  |  | 69KV IED故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.69KV_IED_FA | 69KV IED故障 | OTHER |  |  |  |  | CDC | 184 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | Lights1 | 所內開關場路燈照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0262 |  | 0045 | 1-30-06 |  | 1-2D | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.開關場照明(A) | 所內開關場路燈照明 | OTHER |  |  |  |  | CDC | 185 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 1-30-08 |  |  | 所內用電警報 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 186 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 1-32-12 |  |  | ACB 1S |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 187 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0301 |  |  | 1-32-13 |  |  | ACB 2S |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 188 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0260 |  |  | 1-30-04 |  |  | DC 接地 |  |  |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 189 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 1-31-10 |  |  | 69KV CB 重故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.69KV_CBA | 69KV斷路器重故障 | OTHER |  |  |  |  | CDC | 190 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0281 |  |  | 1-31-09 |  |  | 69KV CB 輕故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.69KV_CBF | 69KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 191 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0284 |  |  | 1-31-12 |  |  | 11KV CB 重故障 |  |  |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.11KV_CBA | 11KV斷路器重故障 | OTHER |  |  |  |  | CDC | 192 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0283 |  |  | 1-31-11 |  |  | 11KV CB 輕故障 |  |  |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.11KV_CBF | 11KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 193 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0271 |  |  | 1-30-15 |  |  | 洩油池泵警報 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 194 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0287 |  |  | 1-31-15 |  |  | 69KV ABS AL |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 195 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 1-30-14 |  |  | NFB 跳脫監視 |  |  |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.直流電源DCA | 直流NFB跳脫監視 | OTHER |  |  |  |  | CDC | 196 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 1-37-00 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 197 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 通訊OLTE重故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0369 |  |  | 1-37-01 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER |  |  |  |  | CDC | 198 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 通訊OLTE輕故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0370 |  |  | 1-37-02 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER |  |  |  |  | CDC | 199 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 通訊PCM警報 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0371 |  |  | 1-37-03 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 200 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | Door2 | 門禁小門 | Element | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0261 |  |  | 1-30-05 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.門禁小門 | 門禁小門 | OTHER |  |  |  |  | CDC | 201 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | NORMAL/ALARM | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | Lights | A/M | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0263 |  | 0046 | 1-30-07 |  | 1-2E | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.開關場照明A/M | 開關場照明自動手動 | OTHER |  |  |  |  | CDC | 202 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 |  |  | USE/LOCK | USE
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | Water1 | 變電所低水位 | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0265 |  |  | 1-30-09 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.變電所低水位 | 變電所低水位 | OTHER |  |  |  |  | CDC | 203 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 保全設定 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0267 |  |  | 1-30-11 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.安全監控 | 安全監控 | OTHER |  |  |  |  | CDC | 204 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | RTU | RTU |  | DCA |  | B3,Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0302 |  |  | 1-32-14 |  |  | RTU DC 電源故障 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.RTU_DC故障 | RTU DC故障 | OTHER |  |  |  |  | CDC | 205 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 1-30-10 |  |  | Locate Empty |  |  |  |  | ELEM/S77_D1 | [8 empty] | 佳二SS.火災警報 | 火警 | OTHER |  |  |  |  | CDC | 206 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 水氣霧故障 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0272 |  |  | 1-31-00 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.水氣霧故障 | 水氣霧故障 | OTHER |  |  |  |  | CDC | 207 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 水氣霧警報 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0273 |  |  | 1-31-01 |  |  | Locate Empty |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.水氣霧警報 | 水氣霧警報 | OTHER |  |  |  |  | CDC | 208 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | ALM_RES | 全所30RY_A/S | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0165 |  | 0087 | 1-14-05 |  | 1-57 | 全所故障指示器復歸點 |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER |  |  |  |  | CDC | 209 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/RESET | RESET
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 佳安線 (F6) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳安線KVAR | 11KV佳安線 KVAR | FEEDER |  |  |  |  | CDC | 210 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 佳安線 (F6) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳安線A1 | 11KV佳安線 R相AMP | FEEDER |  |  |  |  | CDC | 211 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 佳安線 (F6) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳安線A2 | 11KV佳安線 S相AMP | FEEDER |  |  |  |  | CDC | 212 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 佳安線 (F6) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳安線A3 | 11KV佳安線 T相AMP | FEEDER |  |  |  |  | CDC | 213 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 佳安線 (F6) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳安線A0 | 11KV佳安線 N相AMP | FEEDER |  |  |  |  | CDC | 214 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 佳坪線 (F4) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳坪線KVAR | 11KV佳坪線 KVAR | FEEDER |  |  |  |  | CDC | 215 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 佳坪線 (F4) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳坪線A1 | 11KV佳坪線 R相AMP | FEEDER |  |  |  |  | CDC | 216 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 佳坪線 (F4) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳坪線A2 | 11KV佳坪線 S相AMP | FEEDER |  |  |  |  | CDC | 217 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 佳坪線 (F4) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳坪線A3 | 11KV佳坪線 T相AMP | FEEDER |  |  |  |  | CDC | 218 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 佳坪線 (F4) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳坪線A0 | 11KV佳坪線 N相AMP | FEEDER |  |  |  |  | CDC | 219 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 佳洲線 (F8) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳洲線KVAR | 11KV佳洲線 KVAR | FEEDER |  |  |  |  | CDC | 220 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 佳洲線 (F8) R 相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳洲線A1 | 11KV佳洲線 R相AMP | FEEDER |  |  |  |  | CDC | 221 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 佳洲線 (F8) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳洲線A2 | 11KV佳洲線 S相AMP | FEEDER |  |  |  |  | CDC | 222 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 佳洲線 (F8) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳洲線A3 | 11KV佳洲線 T相AMP | FEEDER |  |  |  |  | CDC | 223 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 佳洲線 (F8) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳洲線A0 | 11KV佳洲線 N相AMP | FEEDER |  |  |  |  | CDC | 224 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 佳頂線 (F3) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳頂線KVAR | 11KV佳頂線 KVAR | FEEDER |  |  |  |  | CDC | 225 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 佳頂線 (F3) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳頂線A1 | 11KV佳頂線 R相AMP | FEEDER |  |  |  |  | CDC | 226 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 佳頂線 (F3) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳頂線A2 | 11KV佳頂線 S相AMP | FEEDER |  |  |  |  | CDC | 227 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 佳頂線 (F3) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳頂線A3 | 11KV佳頂線 T相AMP | FEEDER |  |  |  |  | CDC | 228 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 佳頂線 (F3) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳頂線A0 | 11KV佳頂線 N相AMP | FEEDER |  |  |  |  | CDC | 229 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 佳華線 (F7) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳華線KVAR | 11KV佳華線 KVAR | FEEDER |  |  |  |  | CDC | 230 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 佳華線 (F7) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳華線A1 | 11KV佳華線 R相AMP | FEEDER |  |  |  |  | CDC | 231 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 佳華線 (F7) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳華線A2 | 11KV佳華線 S相AMP | FEEDER |  |  |  |  | CDC | 232 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 佳華線 (F7) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳華線A3 | 11KV佳華線 T相AMP | FEEDER |  |  |  |  | CDC | 233 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 佳華線 (F7) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳華線A0 | 11KV佳華線 N相AMP | FEEDER |  |  |  |  | CDC | 234 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | KVAR |  | INSERT | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 佳農線 (F2) 乏 |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳農線KVAR | 11KV佳農線 KVAR | FEEDER |  |  |  |  | CDC | 235 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | I_R |  | INSERT | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 佳農線 (F2) R相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳農線A1 | 11KV佳農線 R相AMP | FEEDER |  |  |  |  | CDC | 236 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | I_S |  | INSERT | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 佳農線 (F2) S相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳農線A2 | 11KV佳農線 S相AMP | FEEDER |  |  |  |  | CDC | 237 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | I_T |  | INSERT | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 佳農線 (F2) T相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳農線A3 | 11KV佳農線 T相AMP | FEEDER |  |  |  |  | CDC | 238 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | I_N |  | INSERT | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 佳農線 (F2) N相電流 |  |  | A_-600_600(-2000_2000) |  | B2/S77_D1 | [8 empty] | 佳二SS.佳農線A0 | 11KV佳農線 N相AMP | FEEDER |  |  |  |  | CDC | 239 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | StaDev | 所內設施 |  | DCV |  | INSERT | MvMoment | 直流電源電壓(P-N) |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | DC 電壓 |  |  | DCVolt_-50_50(-2000_2000) |  | B3/S77_D1 | [8 empty] | 佳二SS.直流電源電壓 | 直流電源電壓 | OTHER |  |  |  |  | CDC | 240 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [5 empty] | LG_24 | 29 | 31 | 32 | 40 | 0.2 | 21 | 19 | 18 | 0 | 0.1 | 0.01 | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | #6DTR 63Q |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_63Q | #6MTR ULTC電驛動作 | OTHER | [5 empty] | 241 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #6DTR 96B1 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_96B1 | #6MTR 撲氣電驛警報 | OTHER | [5 empty] | 242 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #6DTR 96B2 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_96B2 | #6MTR 撲氣電驛動作 | OTHER | [5 empty] | 243 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | #6DTR 96D |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_96D | #6MTR 放壓電驛動作 | OTHER | [5 empty] | 244 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | #6DTR 96P |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_96P | #6MTR 突壓電驛動作 | OTHER | [5 empty] | 245 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 63Q |  | INSERT | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | #7DTR 63Q |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_63Q | #7MTR ULTC電驛動作 | OTHER | [5 empty] | 246 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 96B1 |  | INSERT | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #7DTR 96B1 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_96B1 | #7MTR 撲氣電驛警報 | OTHER | [5 empty] | 247 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 96B2 |  | INSERT | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #7DTR 96B2 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_96B2 | #7MTR 撲氣電驛動作 | OTHER | [5 empty] | 248 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 96D |  | INSERT | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | #7DTR 96D |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_96D | #7MTR 放壓電驛動作 | OTHER | [5 empty] | 249 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 96P |  | INSERT | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | #7DTR 96P |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_96P | #7MTR 突壓電驛動作 | OTHER | [5 empty] | 250 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0497 |  |  | 1-3F-01 |  |  | 佳安線 (F6) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN11_LOA | 佳安線 復閉失敗閉鎖 | OTHER | [5 empty] | 251 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0498 |  |  | 1-3F-02 |  |  | 佳華線 (F7) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN12_LOA | 佳華線 復閉失敗閉鎖 | OTHER | [5 empty] | 252 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0499 |  |  | 1-3F-03 |  |  | 佳洲線 (F8) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN13_LOA | 佳洲線 復閉失敗閉鎖 | OTHER | [5 empty] | 253 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0500 |  |  | 1-3F-04 |  |  | 佳14線 (F9) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN14_LOA | 佳14線 復閉失敗閉鎖 | OTHER | [5 empty] | 254 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0501 |  |  | 1-3F-05 |  |  | 佳15線 (F10) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN15_LOA | 佳15線 復閉失敗閉鎖 | OTHER | [5 empty] | 255 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0496 |  |  | 1-3F-00 |  |  | 佳16線 (F5) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN16_LOA | 佳16線 復閉失敗閉鎖 | OTHER | [5 empty] | 256 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0495 |  |  | 1-3E-15 |  |  | 佳坪線 (F4) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN17_LOA | 佳坪線 復閉失敗閉鎖 | OTHER | [5 empty] | 257 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0494 |  |  | 1-3E-14 |  |  | 佳頂線 (F3) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN18_LOA | 佳頂線 復閉失敗閉鎖 | OTHER | [5 empty] | 258 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0493 |  |  | 1-3E-13 |  |  | 佳農線 (F2) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN19_LOA | 佳農線 復閉失敗閉鎖 | OTHER | [5 empty] | 259 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | LOA |  | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0492 |  |  | 1-3E-12 |  |  | 佳20線 (F1) LOA |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.KN20_LOA | 佳20線 復閉失敗閉鎖 | OTHER | [5 empty] | 260 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | M6 | #6MTR(M6) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | #6TR 二次 (#6MT) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.#6_MAIN_51NA | #6MCB GDA | OTHER | [5 empty] | 261 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | M7 | #7MTR(M7) |  | 51NA |  | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #7TR 二次 (#7MT) 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.#7_MAIN_51NA | #7MCB GDA | OTHER | [5 empty] | 262 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | DS1 | 861 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0392 | 393 | 0036 | 1-38-08 | 1-38-09 | 1-24 | #6TR (861) DS |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.861_DS | 861(#6MTR) DS | DTR | [5 empty] | 263 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | DS2 | 862 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0394 | 395 | 0037 | 1-38-10 | 1-38-11 | 1-25 | #6TR (862) DS |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.862_DS | 862(#6MTR) DS | DTR | [5 empty] | 264 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | DS1 | 871 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0396 | 397 | 0038 | 1-38-12 | 1-38-13 | 1-26 | #7TR (871) DS |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.871_DS | 871(#7MTR) DS | DTR | [5 empty] | 265 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | DS2 | 872 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0398 | 399 | 0039 | 1-38-14 | 1-38-15 | 1-27 | #7TR (872) DS |  |  |  |  | B3/S77_D1 | [8 empty] | 佳二SS.872_DS | 872(#7MTR) DS | DTR | [5 empty] | 266 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S77 | 佳里二SS | 11 | 11kV | TIE6 | TIE(TIE6) |  | CB | #7-#6 | INSERT | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/6BUS | B/7BUS |  |  | 0101 |  | 0050 | 1-0C-05 |  | 1-32 | #7- #6 TIE CB |  |  |  | zzzz | B2/S77_D1 | [8 empty] | 佳二SS.TIE6_CB | 11KV #7-#6 TIE CB | TIE | [5 empty] | 267 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | TIE6 | TIE(TIE6) |  | 51A | #7-#6 | INSERT | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | #7- #6 TIE 51 RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.TIE6_51A | 11KV #7-#6 TIE 51RY | TIE | [5 empty] | 268 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | TIE6 | TIE(TIE6) |  | 51NA | #7-#6 | INSERT | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | #7- #6 TIE 51N RY |  |  |  |  | B2/S77_D1 | [8 empty] | 佳二SS.TIE6_51NA | 11KV #7-#6 TIE 51N RY | TIE | [5 empty] | 269 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0001 |  |  | 1-41 |  |  | 佳農線 (F2) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 270 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0002 |  |  | 1-42 |  |  | 佳頂線 (F3) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 271 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0003 |  |  | 1-43 |  |  | 佳坪線 (F4) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 272 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0005 |  |  | 1-45 |  |  | 佳安線 (F6) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 273 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0006 |  |  | 1-46 |  |  | 佳華線 (F7) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 274 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | kWh |  |  | cv60mAc | kWh RawCount |  | Y |  | ACC | [6 empty] | 0007 |  |  | 1-47 |  |  | 佳洲線 (F8) KWH(+) |  |  |  |  | B2/S77_D1 | [8 empty] | Point Empty | [6 empty] | CDC | 275 | AI_FEEDER | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | TE0 | 860TE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S77_D1 | [8 empty] | 佳二SS.860TE | 860TE (非取樣點) | DTR | [5 empty] | 276 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | BE0 | 860BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S77_D1 | [8 empty] | 佳二SS.860BE | 860BE (非取樣點) | DTR | [5 empty] | 277 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | TE0 | 870TE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S77_D1 | [8 empty] | 佳二SS.870TE | 870TE (非取樣點) | DTR | [5 empty] | 278 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | BE0 | 870BE (非取樣點) | DELETE | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/S77_D1 | [8 empty] | 佳二SS.870BE | 870BE (非取樣點) | DTR | [5 empty] | 279 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | TIE6 | TIE(TIE6) |  | D1 | #7-#6(非取樣點) | INSERT | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.TIE6_DS | #7-#6 TIE_DS (非取樣點) | TIE | [5 empty] | 280 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | 1AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值1 |  | Y |  | AI | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.260_SC_CAP | 11KV#6SC 容量 | SC | [5 empty] | 281 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 11 | 11kV | 270 | #2SC(220) |  | 2AI_Oth | (非取樣點) | INSERT | MvMoment | 暫時AI值2 |  | Y |  | AI | [17 empty] | B2/S77_D1 | [8 empty] | 佳二SS.270_SC_CAP | 11KV#7SC 容量 | SC | [5 empty] | 282 | [10 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 |  |  | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0481 |  |  | 1-3E-01 |  |  | #6DTR 51ZLS |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_51ZUL | #6MTR 51Z U/L | OTHER | [5 empty] | 283 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | #6DTR 86A |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_86A | #6MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 284 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0480 |  |  | 1-3E-00 |  |  | #6DTR 87LS2S |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#6MTR_87UL2 | #6MTR 第二套87RY U/L | OTHER | [5 empty] | 285 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 51Z_UL |  | INSERT | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0483 |  |  | 1-3E-03 |  |  | #7DTR 51ZLS |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_51ZUL | #7MTR 51Z U/L | OTHER | [5 empty] | 286 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | MTR_86A |  | INSERT | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | #7DTR 86A |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_86A | #7MTR 86(51Z/87/96)RY | OTHER | [5 empty] | 287 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | 1_87UL2 |  | INSERT | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0482 |  |  | 1-3E-02 |  |  | #7DTR 87LS2S |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.#7MTR_87UL2 | #7MTR 第二套87RY U/L | OTHER | [5 empty] | 288 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS |  |  | MTR | MTR |  | IRFA |  | INSERT | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 1-3E-08 |  |  | 主變壓器差動電驛IED故障 |  |  |  |  | B1/S77_D1 | [8 empty] | 佳二SS.MTR_IED故障 | MTR IED故障 | OTHER | [5 empty] | 289 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
S77 | 佳里二SS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0024 |  |  | 1-98 |  |  | #6 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aaa | B2/S77_D1 | [8 empty] | 佳二SS.11KV#6BUS_KV | 11KV #6BUS KV | BUS |  |  |  |  | CDC | 2 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S77 | 佳里二SS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0024 |  |  | 1-98 |  |  | #6 11KV 電壓 |  |  | kV_-9_9(-2000_2000) | aab | B2/S77_D1 | [8 empty] | 佳二SS.11KV#6BUS_KV | 11KV #6BUS KV | BUS |  |  |  |  | CDC | 2 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/S77_D1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_2 | OPRD1: S77/11/M6/MW; OPRD2: S77/11/M7/MW
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/S77_D1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: S77/0/CalcPoint/OPRN2_MW
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/S77_D1 | [17 empty] | none
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/S77_D1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: NULL; OPRD2: S77/0/CalcPoint/OPRN2; OPRD3: S77/0/CalcPoint/PRFL_UL
S77 | 佳里二SS |  |  | 6MTR | 6MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S77_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S77/11/M6/MW; OPRD2: S77/11/M6/MVAR; OPRD3: NULL
S77 | 佳里二SS |  |  | 7MTR | 7MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/S77_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: S77/11/M7/MW; OPRD2: S77/11/M7/MVAR; OPRD3: NULL
S77 | 佳里二SS | 11 | 11kV | 6BUS | #6BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S77_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S77/11/6BUS/V
S77 | 佳里二SS | 11 | 11kV | 7BUS | #7BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B2/S77_D1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: S77/11/7BUS/V
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S77_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 佳二SS.#6MTR_MVA | #6MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S77/11/M6/MW; OPRD2: S77/11/M6/MVAR
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/S77_D1 | LG_25 | 23.75 | 27.5 | 31.25 | 50 | 1 | -23.75 | -27.5 | -31.25 | -50 |  |  | 佳二SS.#7MTR_MVA | #7MTR二次側 MVA | DTR | MVA_CAL | LG_25 | va_million | OPRD1: S77/11/M7/MW; OPRD2: S77/11/M7/MVAR
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | LOAD | [9 empty] | B1/S77_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S77//6MTR/MVA; OPRD2: 0
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | LOAD | [9 empty] | B1/S77_D1 | [15 empty] | TR_LOAD_12_5 |  | tr_loading | OPRD1: S77//7MTR/MVA; OPRD2: 0
S77 | 佳里二SS |  |  | 6MTR | #6MTR |  | PF | [9 empty] | B1/S77_D1 | [12 empty] | 佳二SS.#6MTR_PF | #6MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S77/11/M6/MW; OPRD2: S77/11/M6/MVAR
S77 | 佳里二SS |  |  | 7MTR | #7MTR |  | PF | [9 empty] | B1/S77_D1 | [12 empty] | 佳二SS.#7MTR_PF | #7MTR 功率因素 | DTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: S77/11/M7/MW; OPRD2: S77/11/M7/MVAR
S77 | 佳里二SS |  |  | 6MTR | 6MTR |  | TR_PERM | [9 empty] | B1/S77_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S77//6MTR/SupLocal; OPRD2: S77//6MTR/Tap Chan; OPRD3: NULL
S77 | 佳里二SS |  |  | 7MTR | 7MTR |  | TR_PERM | [9 empty] | B1/S77_D1 | [15 empty] | MTR_PERM |  | mtr_perm | OPRD1: S77//7MTR/SupLocal; OPRD2: S77//7MTR/Tap Chan; OPRD3: NULL
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/6BUS/V; OPRD2: S77/11/KN11/I_R; OPRD3: S77/11/KN11/I_S; OPRD4: S77/11/KN11/I_T
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/6BUS/V; OPRD2: S77/11/KN12/I_R; OPRD3: S77/11/KN12/I_S; OPRD4: S77/11/KN12/I_T
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/6BUS/V; OPRD2: S77/11/KN13/I_R; OPRD3: S77/11/KN13/I_S; OPRD4: S77/11/KN13/I_T
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/6BUS/V; OPRD2: S77/11/KN14/I_R; OPRD3: S77/11/KN14/I_S; OPRD4: S77/11/KN14/I_T
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/6BUS/V; OPRD2: S77/11/KN15/I_R; OPRD3: S77/11/KN15/I_S; OPRD4: S77/11/KN15/I_T
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/7BUS/V; OPRD2: S77/11/KN16/I_R; OPRD3: S77/11/KN16/I_S; OPRD4: S77/11/KN16/I_T
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/7BUS/V; OPRD2: S77/11/KN17/I_R; OPRD3: S77/11/KN17/I_S; OPRD4: S77/11/KN17/I_T
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/7BUS/V; OPRD2: S77/11/KN18/I_R; OPRD3: S77/11/KN18/I_S; OPRD4: S77/11/KN18/I_T
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/7BUS/V; OPRD2: S77/11/KN19/I_R; OPRD3: S77/11/KN19/I_S; OPRD4: S77/11/KN19/I_T
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: S77/11/7BUS/V; OPRD2: S77/11/KN20/I_R; OPRD3: S77/11/KN20/I_S; OPRD4: S77/11/KN20/I_T
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN11/kVA; OPRD2: S77/11/KN11/KVAR
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN12/kVA; OPRD2: S77/11/KN12/KVAR
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN13/kVA; OPRD2: S77/11/KN13/KVAR
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN14/kVA; OPRD2: S77/11/KN14/KVAR
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN15/kVA; OPRD2: S77/11/KN15/KVAR
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN16/kVA; OPRD2: S77/11/KN16/KVAR
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN17/kVA; OPRD2: S77/11/KN17/KVAR
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN18/kVA; OPRD2: S77/11/KN18/KVAR
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN19/kVA; OPRD2: S77/11/KN19/KVAR
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/S77_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: S77/11/KN20/kVA; OPRD2: S77/11/KN20/KVAR
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/S77_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S77/11/M6/MW; OPRD2: S77/11/M7/MW
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/S77_D1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: S77/11/M6/MVAR; OPRD2: S77/11/M7/MVAR
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S77_D1 | [12 empty] | 佳二SS.260_SC_MVAR | 11KV#6SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S77/11/260/CB; OPRD2: 6.9; OPRD3: 0
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/S77_D1 | [12 empty] | 佳二SS.270_SC_MVAR | 11KV#7SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: S77/11/270/CB; OPRD2: 6.9; OPRD3: 0
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/S77_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_16 | OPRD1: S77//6MTR/96B1; OPRD2: S77//6MTR/TRA; OPRD3: S77//6MTR/63Q; OPRD4: S77//6MTR/96PA; OPRD5: S77//6MTR/87A; OPRD6: S77//6MTR/51ZA; OPRD7: S77//6MTR/96B2; OPRD8: S77//6MTR/96D; OPRD9: S77//7MTR/96B2; OPRD10: S77//7MTR/96D; OPRD11: S77//7MTR/63Q; OPRD12: S77//7MTR/96B1; OPRD13: S77//7MTR/87A; OPRD14: S77//7MTR/51ZA; OPRD15: S77//7MTR/96PA; OPRD16: S77//7MTR/TRA
S77 | 佳里二SS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/S77_D1 | [15 empty] | STATION_FAULT_1 |  | com_alarm_2 | OPRD1: S77//6MTR/TRF; OPRD2: S77//7MTR/TRF
S77 | 佳里二SS | 0 |  | RTU_A1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/S77_A1 | [17 empty] | lamp2CC | OPRD1: S77/0/RTU/RTU_R_L
S77 | 佳里二SS | 0 |  | StaDev_A1 | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | ELEM/S77_A1 | [17 empty] | lamp2CC | OPRD1: S77/0/StaDev/PSF
S77 | 佳里二SS | 0 |  | StaDev_A1 | 所內設施 |  | PMA | PM通訊故障 |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S77_A1 | [17 empty] | lamp2CC | OPRD1: S77/0/StaDev/PMA
S77 | 佳里二SS | 69 | 69kV | ComPoint_D1 |  |  | CFA | 69KV IED通訊故障 | [8 empty] | B3/S77_D1 | [17 empty] | lamp2CC | OPRD1: S77/69/ComPoint/CFA
S77 | 佳里二SS | 69 | 69kV | ComPoint_D1 |  |  | IRFA | 69KV IED故障 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP |  | B3/S77_D1 | [17 empty] | lamp2CC | OPRD1: S77/69/ComPoint/IRFA
S77 | 佳里二SS | 0 |  | StaDev_A1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S77_A1 | [17 empty] | lamp2CC | OPRD1: S77/0/StaDev/DCE
S77 | 佳里二SS | 69 | 69kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/S77_D1 | [17 empty] | lamp2CC | OPRD1: S77/69/ComPoint/CBA
S77 | 佳里二SS | 69 | 69kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | B3/S77_D1 | [17 empty] | lamp2CC | OPRD1: S77/69/ComPoint/CBF
S77 | 佳里二SS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | B3/S77_D1 | [17 empty] | lamp2CC | OPRD1: S77/69/ComPoint/ABS_89A
S77 | 佳里二SS | 0 |  | StaDev_A1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/S77_A1 | [17 empty] | lamp2CC | OPRD1: S77/0/StaDev/DCA
S77 | 佳里二SS | 0 |  | StaDev_A1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/S77_A1 | [17 empty] | lamp2CC | OPRD1: S77/0/StaDev/Fire

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
S77 | 佳里二SS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 佳二SS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_69KV_1 |  |  | 2 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳安線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳安線KVA | 11KV佳安線KVA | FEEDER |  |  | KVA_CAL |  |  | 3 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳安線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳安線KW | 11KV佳安線KW | FEEDER |  |  | KW_CAL |  |  | 4 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳坪線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳坪線KVA | 11KV佳坪線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳坪線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳坪線KW | 11KV佳坪線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳洲線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳洲線KVA | 11KV佳洲線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳洲線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳洲線KW | 11KV佳洲線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳頂線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳頂線KVA | 11KV佳頂線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳頂線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳頂線KW | 11KV佳頂線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳華線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳華線KVA | 11KV佳華線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳華線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳華線KW | 11KV佳華線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳農線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳農線KVA | 11KV佳農線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳農線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳農線KW | 11KV佳農線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_MVA | #6MTR二次側 MVA | DTR | S77//6MTR/MVA |  | MVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_PF | #6MTR 功率因素 | DTR | S77//6MTR/PF |  | RPDC_PF_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR二次側 |  | MVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_MVA | #7MTR二次側 MVA | DTR | S77//7MTR/MVA |  | MVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_25 | 22.500000 | 27.500000 | 30.000000 | 32.500000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | PF | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_PF | #7MTR 功率因素 | DTR | S77//7MTR/PF |  | RPDC_PF_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
S77 | 佳里二SS | 11 | 11kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_SC_MVAR | 11KV#6SC MVAR | SC | S77/11/260/MVAR |  | SC_CAL_11 |  |  | 19 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 11 | 11kV | 270_SC | #7SC | 6 | MVAR | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_SC_MVAR | 11KV#7SC MVAR | SC | S77/11/270/MVAR |  | SC_CAL_11 |  |  | 20 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳14線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳14線KVA | 11KV佳14線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳14線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳14線KW | 11KV佳14線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳15線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳15線KVA | 11KV佳15線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳15線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳15線KW | 11KV佳15線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳20線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳20線KVA | 11KV佳20線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳20線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳20線KW | 11KV佳20線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳16線KVA | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳16線KVA | 11KV佳16線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  |  |  |  | 佳16線KW | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.佳16線KW | 11KV佳16線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 69 | 69kV | _CBA | 斷路器重故障(_CBA) | [27 empty] | ADCS_N | [8 empty] | 佳二SS.69KV_CBA_A | 69KV斷路器重故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 29 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | _CBF | 斷路器輕故障(_CBF) | [27 empty] | ADCS_N | [8 empty] | 佳二SS.69KV_CBF_A | 69KV斷路器輕故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 30 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | SC警報 | SC警報 | [27 empty] | ADCS_N | [8 empty] | 佳二SS.69KVSC警報_A | 69KVSC警報 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 31 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | RTU_DC故障 | RTU | [27 empty] | ADCS_N | [8 empty] | 佳二SS.RTU_DC故障_A | RTU DC故障 (AD) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 32 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR_MVA | #6MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_MVA_4 | #6MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 33 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_PERM | #6MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 34 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR_MVA | #7MTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_MVA_4 | #7MTR MVA 點燈 (D4) | DTR |  |  | MAP_SET |  |  | 35 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | PERM | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_PERM | #7MTR TAP PERMISSION POINT | DTR |  |  | DTR_PERM |  |  | 36 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
S77 | 佳里二SS | 69 | 69kV | _IED_CFA | IED通訊故障 | [27 empty] | ADCS_N | [8 empty] | 佳二SS.69KV_IED_CFA_A | 69KV IED通訊故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 37 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | _IED_FA | IED故障 | [27 empty] | ADCS_N | [8 empty] | 佳二SS.69KV_IED_FA_A | 69KV IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 38 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 81RY_IED_FA | 低頻IED故障 | [27 empty] | ADCS_N | [8 empty] | 佳二SS.81RY_IED_FA_A | 低頻IED故障 (AD) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 39 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | S77/0/RTU/ADCH1 |  |  |  | CDC | 40 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | S77/0/RTU/ADCH2 |  |  |  | CDC | 41 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | S77/0/RTU/ADCL1 |  |  |  | CDC | 42 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | S77/0/RTU/ADCL2 |  |  |  | CDC | 43 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 佳二SS.69KV#1BUS_KV | 69KV #1BUS KV | BUS |  |  |  |  | CDC | 44 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
S77 | 佳里二SS | 11 | 11kV | 6BUS | #6BUS |  | V | [17 empty] | 1-98 | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.11KV#6BUS_KV | 11KV #6BUS KV | BUS | S77/11/6BUS/V |  |  |  | CDC | 45 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S77 | 佳里二SS | 11 | 11kV | 7BUS | #7BUS |  | V | [17 empty] | 1-BC | [5 empty] | kV_-9_9(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.11KV#7BUS_KV | 11KV #7BUS KV | BUS | S77/11/7BUS/V |  |  |  | CDC | 46 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
S77 | 佳里二SS | 11 | 11kV | 佳安線 | 佳安線 |  | 佳安線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳安線KVAR | 11KV佳安線 KVAR | FEEDER | S77/11/KN11/KVAR |  |  |  | CDC | 47 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳安線 | 佳安線 |  | 佳安線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳安線A1 | 11KV佳安線 R相AMP | FEEDER | S77/11/KN11/I_R |  |  |  | CDC | 48 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳安線 | 佳安線 |  | 佳安線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳安線A2 | 11KV佳安線 S相AMP | FEEDER | S77/11/KN11/I_S |  |  |  | CDC | 49 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳安線 | 佳安線 |  | 佳安線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳安線A3 | 11KV佳安線 T相AMP | FEEDER | S77/11/KN11/I_T |  |  |  | CDC | 50 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳安線 | 佳安線 |  | 佳安線A0 | [17 empty] | 1-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳安線A0 | 11KV佳安線 N相AMP | FEEDER | S77/11/KN11/I_N |  |  |  | CDC | 51 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳坪線 | 佳坪線 |  | 佳坪線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳坪線KVAR | 11KV佳坪線 KVAR | FEEDER | S77/11/KN17/KVAR |  |  |  | CDC | 52 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳坪線 | 佳坪線 |  | 佳坪線A1 | [17 empty] | 1-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳坪線A1 | 11KV佳坪線 R相AMP | FEEDER | S77/11/KN17/I_R |  |  |  | CDC | 53 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳坪線 | 佳坪線 |  | 佳坪線A2 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳坪線A2 | 11KV佳坪線 S相AMP | FEEDER | S77/11/KN17/I_S |  |  |  | CDC | 54 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳坪線 | 佳坪線 |  | 佳坪線A3 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳坪線A3 | 11KV佳坪線 T相AMP | FEEDER | S77/11/KN17/I_T |  |  |  | CDC | 55 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳坪線 | 佳坪線 |  | 佳坪線A0 | [17 empty] | 1-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳坪線A0 | 11KV佳坪線 N相AMP | FEEDER | S77/11/KN17/I_N |  |  |  | CDC | 56 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳洲線 | 佳洲線 |  | 佳洲線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳洲線KVAR | 11KV佳洲線 KVAR | FEEDER | S77/11/KN13/KVAR |  |  |  | CDC | 57 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳洲線 | 佳洲線 |  | 佳洲線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳洲線A1 | 11KV佳洲線 R相AMP | FEEDER | S77/11/KN13/I_R |  |  |  | CDC | 58 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳洲線 | 佳洲線 |  | 佳洲線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳洲線A2 | 11KV佳洲線 S相AMP | FEEDER | S77/11/KN13/I_S |  |  |  | CDC | 59 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳洲線 | 佳洲線 |  | 佳洲線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳洲線A3 | 11KV佳洲線 T相AMP | FEEDER | S77/11/KN13/I_T |  |  |  | CDC | 60 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳洲線 | 佳洲線 |  | 佳洲線A0 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳洲線A0 | 11KV佳洲線 N相AMP | FEEDER | S77/11/KN13/I_N |  |  |  | CDC | 61 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳頂線 | 佳頂線 |  | 佳頂線KVAR | [17 empty] | 1-A9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳頂線KVAR | 11KV佳頂線 KVAR | FEEDER | S77/11/KN18/KVAR |  |  |  | CDC | 62 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳頂線 | 佳頂線 |  | 佳頂線A1 | [17 empty] | 1-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳頂線A1 | 11KV佳頂線 R相AMP | FEEDER | S77/11/KN18/I_R |  |  |  | CDC | 63 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳頂線 | 佳頂線 |  | 佳頂線A2 | [17 empty] | 1-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳頂線A2 | 11KV佳頂線 S相AMP | FEEDER | S77/11/KN18/I_S |  |  |  | CDC | 64 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳頂線 | 佳頂線 |  | 佳頂線A3 | [17 empty] | 1-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳頂線A3 | 11KV佳頂線 T相AMP | FEEDER | S77/11/KN18/I_T |  |  |  | CDC | 65 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳頂線 | 佳頂線 |  | 佳頂線A0 | [17 empty] | 1-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳頂線A0 | 11KV佳頂線 N相AMP | FEEDER | S77/11/KN18/I_N |  |  |  | CDC | 66 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳華線 | 佳華線 |  | 佳華線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳華線KVAR | 11KV佳華線 KVAR | FEEDER | S77/11/KN12/KVAR |  |  |  | CDC | 67 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳華線 | 佳華線 |  | 佳華線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳華線A1 | 11KV佳華線 R相AMP | FEEDER | S77/11/KN12/I_R |  |  |  | CDC | 68 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳華線 | 佳華線 |  | 佳華線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳華線A2 | 11KV佳華線 S相AMP | FEEDER | S77/11/KN12/I_S |  |  |  | CDC | 69 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳華線 | 佳華線 |  | 佳華線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳華線A3 | 11KV佳華線 T相AMP | FEEDER | S77/11/KN12/I_T |  |  |  | CDC | 70 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳華線 | 佳華線 |  | 佳華線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳華線A0 | 11KV佳華線 N相AMP | FEEDER | S77/11/KN12/I_N |  |  |  | CDC | 71 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳農線 | 佳農線 |  | 佳農線KVAR | [17 empty] | 1-A5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳農線KVAR | 11KV佳農線 KVAR | FEEDER | S77/11/KN19/KVAR |  |  |  | CDC | 72 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳農線 | 佳農線 |  | 佳農線A1 | [17 empty] | 1-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳農線A1 | 11KV佳農線 R相AMP | FEEDER | S77/11/KN19/I_R |  |  |  | CDC | 73 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳農線 | 佳農線 |  | 佳農線A2 | [17 empty] | 1-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳農線A2 | 11KV佳農線 S相AMP | FEEDER | S77/11/KN19/I_S |  |  |  | CDC | 74 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳農線 | 佳農線 |  | 佳農線A3 | [17 empty] | 1-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳農線A3 | 11KV佳農線 T相AMP | FEEDER | S77/11/KN19/I_T |  |  |  | CDC | 75 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳農線 | 佳農線 |  | 佳農線A0 | [17 empty] | 1-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳農線A0 | 11KV佳農線 N相AMP | FEEDER | S77/11/KN19/I_N |  |  |  | CDC | 76 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | _TIE6 | #7-#6 |  | I_R | [17 empty] | 1-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.11KV_TIE6_A1 | 11KV #7-#6 TIE R相AMP | TIE | S77/11/TIE6/I_R |  |  |  | CDC | 77 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | _TIE6 | #7-#6 |  | I_S | [17 empty] | 1-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.11KV_TIE6_A2 | 11KV #7-#6 TIE S相AMP | TIE | S77/11/TIE6/I_S |  |  |  | CDC | 78 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | _TIE6 | #7-#6 |  | I_T | [17 empty] | 1-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.11KV_TIE6_A3 | 11KV #7-#6 TIE T相AMP | TIE | S77/11/TIE6/I_T |  |  |  | CDC | 79 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_MW | #6MTR二次側 MW | DTR | S77/11/M6/MW |  |  |  | CDC | 80 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_MVAR | #6MTR二次側 MVAR | DTR | S77/11/M6/MVAR |  |  |  | CDC | 81 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR二次側 |  | I_R | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_A1 | #6MTR二次側 R相AMP | DTR | S77/11/M6/I_R |  |  |  | CDC | 82 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR二次側 |  | I_S | [17 empty] | 1-9F | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_A2 | #6MTR二次側 S相AMP | DTR | S77/11/M6/I_S |  |  |  | CDC | 83 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR二次側 |  | I_T | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_A3 | #6MTR二次側 T相AMP | DTR | S77/11/M6/I_T |  |  |  | CDC | 84 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_OIL | #6MTR 油溫 | DTR | S77//6MTR/OilTemp |  |  |  | CDC | 85 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_COIL | #6MTR 線溫 | DTR | S77//6MTR/CoilTemp |  |  |  | CDC | 86 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | TapPosMv | [17 empty] | 1-9B |  | 1-39 |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_TAP | #6MTR OLTC TAP | DTR | S77//6MTR/TapPosMv |  |  |  | CDC | 87 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_MW | #7MTR二次側 MW | DTR | S77/11/M7/MW |  |  |  | CDC | 88 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_MVAR | #7MTR二次側 MVAR | DTR | S77/11/M7/MVAR |  |  |  | CDC | 89 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR二次側 |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_A1 | #7MTR二次側 R相AMP | DTR | S77/11/M7/I_R |  |  |  | CDC | 90 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR二次側 |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_A2 | #7MTR二次側 S相AMP | DTR | S77/11/M7/I_S |  |  |  | CDC | 91 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR二次側 |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_A3 | #7MTR二次側 T相AMP | DTR | S77/11/M7/I_T |  |  |  | CDC | 92 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_1205 | 1084.000000 | 1205.000000 | 1325.500000 | 1600.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_OIL | #7MTR 油溫 | DTR | S77//7MTR/OilTemp |  |  |  | CDC | 93 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | CoilTemp | [17 empty] | 1-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_COIL | #7MTR 線溫 | DTR | S77//7MTR/CoilTemp |  |  |  | CDC | 94 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | TapPosMv | [17 empty] | 1-BF |  | 1-4E |  |  |  | TAP_-4.5_12.5(0_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_TAP | #7MTR OLTC TAP | DTR | S77//7MTR/TapPosMv |  |  |  | CDC | 95 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | TAP12_4 | 11.000000 | 11.000000 | 12.000000 | 12.500000 | 0.000000 | -3.000000 | -3.000000 | -4.000000 | -4.500000 | 0.100000
S77 | 佳里二SS | 0 |  |  |  |  | DCV | [17 empty] | 1-83 | [5 empty] | DCVolt_-50_50(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.直流電源電壓 | 直流電源電壓 | OTHER | S77/0/StaDev/DCV |  |  |  | CDC | 96 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_24 | 29.000000 | 31.000000 | 31.000000 | 40.000000 | 0.200000 | 21.000000 | 19.000000 | 19.000000 | 0.000000 | 0.100000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳14線 | 佳14線 |  | 佳14線KVAR | [17 empty] | 1-D3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳14線KVAR | 11KV佳14線 KVAR | FEEDER | S77/11/KN14/KVAR |  |  |  | CDC | 97 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳14線 | 佳14線 |  | 佳14線A1 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳14線A1 | 11KV佳14線 R相AMP | FEEDER | S77/11/KN14/I_R |  |  |  | CDC | 98 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳14線 | 佳14線 |  | 佳14線A2 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳14線A2 | 11KV佳14線 S相AMP | FEEDER | S77/11/KN14/I_S |  |  |  | CDC | 99 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳14線 | 佳14線 |  | 佳14線A3 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳14線A3 | 11KV佳14線 T相AMP | FEEDER | S77/11/KN14/I_T |  |  |  | CDC | 100 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳14線 | 佳14線 |  | 佳14線A0 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳14線A0 | 11KV佳14線 N相AMP | FEEDER | S77/11/KN14/I_N |  |  |  | CDC | 101 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳15線 | 佳15線 |  | 佳15線KVAR | [17 empty] | 1-D7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳15線KVAR | 11KV佳15線 KVAR | FEEDER | S77/11/KN15/KVAR |  |  |  | CDC | 102 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳15線 | 佳15線 |  | 佳15線A1 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳15線A1 | 11KV佳15線 R相AMP | FEEDER | S77/11/KN15/I_R |  |  |  | CDC | 103 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳15線 | 佳15線 |  | 佳15線A2 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳15線A2 | 11KV佳15線 S相AMP | FEEDER | S77/11/KN15/I_S |  |  |  | CDC | 104 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳15線 | 佳15線 |  | 佳15線A3 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳15線A3 | 11KV佳15線 T相AMP | FEEDER | S77/11/KN15/I_T |  |  |  | CDC | 105 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳15線 | 佳15線 |  | 佳15線A0 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳15線A0 | 11KV佳15線 N相AMP | FEEDER | S77/11/KN15/I_N |  |  |  | CDC | 106 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳20線 | 佳20線 |  | 佳20線KVAR | [17 empty] | 1-A1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳20線KVAR | 11KV佳20線 KVAR | FEEDER | S77/11/KN20/KVAR |  |  |  | CDC | 107 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳20線 | 佳20線 |  | 佳20線A1 | [17 empty] | 1-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳20線A1 | 11KV佳20線 R相AMP | FEEDER | S77/11/KN20/I_R |  |  |  | CDC | 108 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳20線 | 佳20線 |  | 佳20線A2 | [17 empty] | 1-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳20線A2 | 11KV佳20線 S相AMP | FEEDER | S77/11/KN20/I_S |  |  |  | CDC | 109 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳20線 | 佳20線 |  | 佳20線A3 | [17 empty] | 1-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳20線A3 | 11KV佳20線 T相AMP | FEEDER | S77/11/KN20/I_T |  |  |  | CDC | 110 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳20線 | 佳20線 |  | 佳20線A0 | [17 empty] | 1-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳20線A0 | 11KV佳20線 N相AMP | FEEDER | S77/11/KN20/I_N |  |  |  | CDC | 111 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳16線 | 佳16線 |  | 佳16線KVAR | [17 empty] | 1-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳16線KVAR | 11KV佳16線 KVAR | FEEDER | S77/11/KN16/KVAR |  |  |  | CDC | 112 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳16線 | 佳16線 |  | 佳16線A1 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳16線A1 | 11KV佳16線 R相AMP | FEEDER | S77/11/KN16/I_R |  |  |  | CDC | 113 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳16線 | 佳16線 |  | 佳16線A2 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳16線A2 | 11KV佳16線 S相AMP | FEEDER | S77/11/KN16/I_S |  |  |  | CDC | 114 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳16線 | 佳16線 |  | 佳16線A3 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳16線A3 | 11KV佳16線 T相AMP | FEEDER | S77/11/KN16/I_T |  |  |  | CDC | 115 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | 佳16線 | 佳16線 |  | 佳16線A0 | [17 empty] | 1-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 佳二SS.佳16線A0 | 11KV佳16線 N相AMP | FEEDER | S77/11/KN16/I_N |  |  |  | CDC | 116 | GENERICAIPoint | SS419_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | PHA | [17 empty] | 1-0F-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_PHA | 11KV佳安線(KN11) 相間RY | FEEDER | S77/11/KN11/PHA |  |  |  | CDC | 117 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) |  | GDA | [17 empty] | 1-10-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_GDA | 11KV佳安線(KN11) 接地RY | FEEDER | S77/11/KN11/GDA |  |  |  | CDC | 118 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) 79RY |  | 79UL | [17 empty] | 1-34-07 |  | 1-51 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_79UL | 11KV佳安線(KN11) 79RY U/L | FEEDER | S77/11/KN11/79UL |  |  |  | CDC | 119 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN11 | 佳安線(KN11) LCO分流器 |  | ADJ | [17 empty] | 1-36-05 |  | 1-75 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_ADJ | 11KV佳安線(KN11) LCO分流器 U/L | FEEDER | S77/11/KN11/ADJ |  |  |  | CDC | 120 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN11 | KN(11KV佳安線) |  | CB | [17 empty] | 1-0E-06 |  | 1-49 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_CB | KN11(11KV佳安線) CB | FEEDER | S77/11/KN11/CB |  |  |  | CDC | 121 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_PHA | 11KV佳華線(KN12) 相間RY | FEEDER | S77/11/KN12/PHA |  |  |  | CDC | 122 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_GDA | 11KV佳華線(KN12) 接地RY | FEEDER | S77/11/KN12/GDA |  |  |  | CDC | 123 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) 79RY |  | 79UL | [17 empty] | 1-34-08 |  | 1-52 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_79UL | 11KV佳華線(KN12) 79RY U/L | FEEDER | S77/11/KN12/79UL |  |  |  | CDC | 124 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN12 | 佳華線(KN12) LCO分流器 |  | ADJ | [17 empty] | 1-36-06 |  | 1-76 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_ADJ | 11KV佳華線(KN12) LCO分流器 U/L | FEEDER | S77/11/KN12/ADJ |  |  |  | CDC | 125 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN12 | KN12(11KV佳華線) |  | CB | [17 empty] | 1-0E-07 |  | 1-4A | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_CB | KN12(11KV佳華線) CB | FEEDER | S77/11/KN12/CB |  |  |  | CDC | 126 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | PHA | [17 empty] | 1-10-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_PHA | 11KV佳洲線(KN13) 相間RY | FEEDER | S77/11/KN13/PHA |  |  |  | CDC | 127 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) |  | GDA | [17 empty] | 1-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_GDA | 11KV佳洲線(KN13) 接地RY | FEEDER | S77/11/KN13/GDA |  |  |  | CDC | 128 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) 79RY |  | 79UL | [17 empty] | 1-34-09 |  | 1-53 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_79UL | 11KV佳洲線(KN13) 79RY U/L | FEEDER | S77/11/KN13/79UL |  |  |  | CDC | 129 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN13 | 佳洲線(KN13) LCO分流器 |  | ADJ | [17 empty] | 1-36-07 |  | 1-77 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_ADJ | 11KV佳洲線(KN13) LCO分流器 U/L | FEEDER | S77/11/KN13/ADJ |  |  |  | CDC | 130 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN13 | KN13(11KV佳洲線) |  | CB | [17 empty] | 1-0F-00 |  | 1-4B | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_CB | KN13(11KV佳洲線) CB | FEEDER | S77/11/KN13/CB |  |  |  | CDC | 131 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | PHA | [17 empty] | 1-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_PHA | 11KV佳14線(KN14) 相間RY | FEEDER | S77/11/KN14/PHA |  |  |  | CDC | 132 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) |  | GDA | [17 empty] | 1-10-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_GDA | 11KV佳14線(KN14) 接地RY | FEEDER | S77/11/KN14/GDA |  |  |  | CDC | 133 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) 79RY |  | 79UL | [17 empty] | 1-34-10 |  | 1-54 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_79UL | 11KV佳14線(KN14) 79RY U/L | FEEDER | S77/11/KN14/79UL |  |  |  | CDC | 134 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN14 | 佳14線(KN14) LCO分流器 |  | ADJ | [17 empty] | 1-36-08 |  | 1-78 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_ADJ | 11KV佳14線(KN14) LCO分流器 U/L | FEEDER | S77/11/KN14/ADJ |  |  |  | CDC | 135 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN14 | KN14(11KV佳14線) |  | CB | [17 empty] | 1-0F-01 |  | 1-4C | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_CB | KN14(11KV佳14線) CB | FEEDER | S77/11/KN14/CB |  |  |  | CDC | 136 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_PHA | 11KV佳15線(KN15) 相間RY | FEEDER | S77/11/KN15/PHA |  |  |  | CDC | 137 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_GDA | 11KV佳15線(KN15) 接地RY | FEEDER | S77/11/KN15/GDA |  |  |  | CDC | 138 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) 79RY |  | 79UL | [17 empty] | 1-34-11 |  | 1-55 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_79UL | 11KV佳15線(KN15) 79RY U/L | FEEDER | S77/11/KN15/79UL |  |  |  | CDC | 139 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN15 | 佳15線(KN15) LCO分流器 |  | ADJ | [17 empty] | 1-36-09 |  | 1-79 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_ADJ | 11KV佳15線(KN15) LCO分流器 U/L | FEEDER | S77/11/KN15/ADJ |  |  |  | CDC | 140 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN15 | KN15(11KV佳15線) |  | CB | [17 empty] | 1-0F-02 |  | 1-4D | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_CB | KN15(11KV佳15線) CB | FEEDER | S77/11/KN15/CB |  |  |  | CDC | 141 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | PHA | [17 empty] | 1-0E-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_PHA | 11KV佳16線(KN16) 相間RY | FEEDER | S77/11/KN16/PHA |  |  |  | CDC | 142 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) |  | GDA | [17 empty] | 1-0E-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_GDA | 11KV佳16線(KN16) 接地RY | FEEDER | S77/11/KN16/GDA |  |  |  | CDC | 143 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) 79RY |  | 79UL | [17 empty] | 1-33-11 |  | 1-40 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_79UL | 11KV佳16線(KN16) 79RY U/L | FEEDER | S77/11/KN16/79UL |  |  |  | CDC | 144 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN16 | 佳16線(KN16) LCO分流器 |  | ADJ | [17 empty] | 1-36-04 |  | 1-74 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_ADJ | 11KV佳16線(KN16) LCO分流器 U/L | FEEDER | S77/11/KN16/ADJ |  |  |  | CDC | 145 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN16 | KN16(11KV佳16線) |  | CB | [17 empty] | 1-0C-04 |  | 1-38 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_CB | KN16(11KV佳16線) CB | FEEDER | S77/11/KN16/CB |  |  |  | CDC | 146 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | PHA | [17 empty] | 1-0D-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_PHA | 11KV佳坪線(KN17) 相間RY | FEEDER | S77/11/KN17/PHA |  |  |  | CDC | 147 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) |  | GDA | [17 empty] | 1-0E-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_GDA | 11KV佳坪線(KN17) 接地RY | FEEDER | S77/11/KN17/GDA |  |  |  | CDC | 148 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) 79RY |  | 79UL | [17 empty] | 1-33-10 |  | 1-3F | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_79UL | 11KV佳坪線(KN17) 79RY U/L | FEEDER | S77/11/KN17/79UL |  |  |  | CDC | 149 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN17 | 佳坪線(KN17) LCO分流器 |  | ADJ | [17 empty] | 1-36-03 |  | 1-73 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_ADJ | 11KV佳坪線(KN17) LCO分流器 U/L | FEEDER | S77/11/KN17/ADJ |  |  |  | CDC | 150 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN17 | KN17(11KV佳坪線) |  | CB | [17 empty] | 1-0C-03 |  | 1-37 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_CB | KN17(11KV佳坪線) CB | FEEDER | S77/11/KN17/CB |  |  |  | CDC | 151 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | PHA | [17 empty] | 1-0D-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_PHA | 11KV佳頂線(KN18) 相間RY | FEEDER | S77/11/KN18/PHA |  |  |  | CDC | 152 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_GDA | 11KV佳頂線(KN18) 接地RY | FEEDER | S77/11/KN18/GDA |  |  |  | CDC | 153 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) 79RY |  | 79UL | [17 empty] | 1-33-09 |  | 1-3E | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_79UL | 11KV佳頂線(KN18) 79RY U/L | FEEDER | S77/11/KN18/79UL |  |  |  | CDC | 154 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN18 | 佳頂線(KN18) LCO分流器 |  | ADJ | [17 empty] | 1-36-02 |  | 1-72 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_ADJ | 11KV佳頂線(KN18) LCO分流器 U/L | FEEDER | S77/11/KN18/ADJ |  |  |  | CDC | 155 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN18 | KN18(11KV佳頂線) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_CB | KN18(11KV佳頂線) CB | FEEDER | S77/11/KN18/CB |  |  |  | CDC | 156 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | PHA | [17 empty] | 1-0D-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_PHA | 11KV佳農線(KN19) 相間RY | FEEDER | S77/11/KN19/PHA |  |  |  | CDC | 157 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) |  | GDA | [17 empty] | 1-0D-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_GDA | 11KV佳農線(KN19) 接地RY | FEEDER | S77/11/KN19/GDA |  |  |  | CDC | 158 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) 79RY |  | 79UL | [17 empty] | 1-33-08 |  | 1-3D | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_79UL | 11KV佳農線(KN19) 79RY U/L | FEEDER | S77/11/KN19/79UL |  |  |  | CDC | 159 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN19 | 佳農線(KN19) LCO分流器 |  | ADJ | [17 empty] | 1-36-01 |  | 1-71 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_ADJ | 11KV佳農線(KN19) LCO分流器 U/L | FEEDER | S77/11/KN19/ADJ |  |  |  | CDC | 160 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN19 | KN19(11KV佳農線) |  | CB | [17 empty] | 1-0C-01 |  | 1-35 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_CB | KN19(11KV佳農線) CB | FEEDER | S77/11/KN19/CB |  |  |  | CDC | 161 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | PHA | [17 empty] | 1-0D-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_PHA | 11KV佳20線(KN20) 相間RY | FEEDER | S77/11/KN20/PHA |  |  |  | CDC | 162 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_GDA | 11KV佳20線(KN20) 接地RY | FEEDER | S77/11/KN20/GDA |  |  |  | CDC | 163 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) 79RY |  | 79UL | [17 empty] | 1-33-07 |  | 1-3C | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_79UL | 11KV佳20線(KN20) 79RY U/L | FEEDER | S77/11/KN20/79UL |  |  |  | CDC | 164 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 11 | 11kV | KN20 | 佳20線(KN20) LCO分流器 |  | ADJ | [17 empty] | 1-36-00 |  | 1-70 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_ADJ | 11KV佳20線(KN20) LCO分流器 U/L | FEEDER | S77/11/KN20/ADJ |  |  |  | CDC | 165 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
S77 | 佳里二SS | 11 | 11kV | KN20 | KN20(11KV佳20線) |  | CB | [17 empty] | 1-0C-00 |  | 1-34 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_CB | KN20(11KV佳20線) CB | FEEDER | S77/11/KN20/CB |  |  |  | CDC | 166 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | CB | [17 empty] | 1-00-01 |  | 1-30 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.860_CB | 860(#6MTR) CB | DTR | S77/69/860/CB |  |  |  | CDC | 167 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 6M | #6MTR |  | CB | [17 empty] | 1-00-02 |  | 1-31 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.6M_CB | 6M(#6MTR) CB | DTR | S77/11/M6/CB |  |  |  | CDC | 168 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 51A | [17 empty] | 1-00-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_51A | #6MTR 51RY | DTR | S77/69/860/51A |  |  |  | CDC | 169 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 51NA | [17 empty] | 1-00-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_51NA | #6MTR 51N RY | DTR | S77/69/860/51NA |  |  |  | CDC | 170 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 51ZA | [17 empty] | 1-01-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_51ZA | #6MTR 51Z RY | DTR | S77//6MTR/51ZA |  |  |  | CDC | 171 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 87A | [17 empty] | 1-00-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_87A | #6MTR 87RY | DTR | S77//6MTR/87A |  |  |  | CDC | 172 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 87UL | [17 empty] | 1-33-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_87UL | #6MTR 87RY U/L | DTR | S77//6MTR/87UL |  |  |  | CDC | 173 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 0 |  | 6MTR | #860 |  | 81AS | [17 empty] | 1-0C-06 |  | 1-41 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_81A/S | #860 81RY A/S | DTR | S77//6MTR/81A |  |  |  | CDC | 174 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S77 | 佳里二SS | 0 |  | 6M | #6MTR二次側(6M) |  | 51A | [17 empty] | 1-00-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.6M_51A | #6MTR二次側(6M) 51RY | DTR | S77/11/M6/51A |  |  |  | CDC | 175 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | TRA | [17 empty] | 1-33-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_TRA | #6MTR 重故障 | DTR | S77//6MTR/TRA |  |  |  | CDC | 176 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | TRF | [17 empty] | 1-33-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_TRF | #6MTR 輕故障 | DTR | S77//6MTR/TRF |  |  |  | CDC | 177 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_S/L | #6MTR OLTC S/L | DTR | S77//6MTR/SupLocal |  |  |  | CDC | 178 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | A_M | [17 empty] | 1-33-05 |  | 1-3A | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_A/M | #6MTR OLTC A/M | DTR | S77//6MTR/Tap Chan |  |  |  | CDC | 179 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | OLTC_DLY | [17 empty] | 1-33-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_OLTC遲滯 | #6MTR OLTC遲滯 | DTR | S77//6MTR/OLTC_DLY |  |  |  | CDC | 180 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR_AC | #6MTR |  | FAULT | [17 empty] | 1-33-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_AC_FAULT | #6MTR AC電源失效 | DTR | S77//6MTR/AC_Fault |  |  |  | CDC | 181 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | CB | [17 empty] | 1-01-02 |  | 1-44 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.870_CB | 870(#7MTR) CB | DTR | S77/69/870/CB |  |  |  | CDC | 182 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 7M | #7MTR |  | CB | [17 empty] | 1-01-03 |  | 1-45 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.7M_CB | 7M(#7MTR) CB | DTR | S77/11/M7/CB |  |  |  | CDC | 183 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 51A | [17 empty] | 1-01-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_51A | #7MTR 51RY | DTR | S77/69/870/51A |  |  |  | CDC | 184 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 51NA | [17 empty] | 1-01-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_51NA | #7MTR 51N RY | DTR | S77/69/870/51NA |  |  |  | CDC | 185 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 51ZA | [17 empty] | 1-02-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_51ZA | #7MTR 51Z RY | DTR | S77//7MTR/51ZA |  |  |  | CDC | 186 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 87A | [17 empty] | 1-02-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_87A | #7MTR 87RY | DTR | S77//7MTR/87A |  |  |  | CDC | 187 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 87UL | [17 empty] | 1-34-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_87UL | #7MTR 87RY U/L | DTR | S77//7MTR/87UL |  |  |  | CDC | 188 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 81AS | [17 empty] | 1-0F-04 |  | 1-56 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_81A/S | #7MTR 81RY A/S | DTR | S77//7MTR/81A |  |  |  | CDC | 189 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
S77 | 佳里二SS | 0 |  | 7M | #7MTR二次側(7M) |  | 51A | [17 empty] | 1-02-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.7M_51A | #7MTR二次側(7M) 51RY | DTR | S77/11/M7/51A |  |  |  | CDC | 190 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | TRA | [17 empty] | 1-34-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_TRA | #7MTR 重故障 | DTR | S77//7MTR/TRA |  |  |  | CDC | 191 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_TRF | #7MTR 輕故障 | DTR | S77//7MTR/TRF |  |  |  | CDC | 192 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | SupLocal | [17 empty] | 1-34-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_S/L | #7MTR OLTC S/L | DTR | S77//7MTR/SupLocal |  |  |  | CDC | 193 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | A_M | [17 empty] | 1-34-05 |  | 1-4F | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_A/M | #7MTR OLTC A/M | DTR | S77//7MTR/Tap Chan |  |  |  | CDC | 194 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | OLTC_DLY | [17 empty] | 1-34-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_OLTC遲滯 | #7MTR OLTC遲滯 | DTR | S77//7MTR/OLTC_DLY |  |  |  | CDC | 195 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR_AC | #7MTR |  | FAULT | [17 empty] | 1-34-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_AC_FAULT | #7MTR AC電源失效 | DTR | S77//7MTR/AC_Fault |  |  |  | CDC | 196 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-0B-07 |  | 1-33 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_CB | 260(11KV #6SC) CB | SC | S77/11/260/CB |  |  |  | CDC | 197 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 1-33-06 |  | 1-3B | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_A/M | 11KV #6SC 乏控器 A/M | SC | S77/11/260/SC_A_M |  |  |  | CDC | 198 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_SCA | 11KV #6SC 51,51N RY | SC | S77/11/260/SCA |  |  |  | CDC | 199 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-0D-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | S77/11/260/UVA |  |  |  | CDC | 200 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | CB | [17 empty] | 1-0E-05 |  | 1-48 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_CB | 270(11KV #7SC) CB | SC | S77/11/270/CB |  |  |  | CDC | 201 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | SC_A_M | [17 empty] | 1-34-06 |  | 1-50 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_A/M | 11KV #7SC 乏控器 A/M | SC | S77/11/270/SC_A_M |  |  |  | CDC | 202 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | SCA | [17 empty] | 1-0F-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_SCA | 11KV #7SC 51,51N RY | SC | S77/11/270/SCA |  |  |  | CDC | 203 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 270 | #7SC(270) |  | UVA | [17 empty] | 1-0F-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_UVA | 11KV #7SC 27RY(欠壓) | SC | S77/11/270/UVA |  |  |  | CDC | 204 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 佳二SS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 205 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV |  |  |  | CBA | [17 empty] | 1-31-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.11KV_CBA | 11KV斷路器重故障 | OTHER | S77/11/ComPoint/CBA |  |  |  | CDC | 206 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV |  |  |  | CBF | [17 empty] | 1-31-11 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.11KV_CBF | 11KV斷路器輕故障 | OTHER | S77/11/ComPoint/CBF |  |  |  | CDC | 207 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-31-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | S77/69/ComPoint/ABS_89A |  |  |  | CDC | 208 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-31-10 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.69KV_CBA | 69KV斷路器重故障 | OTHER | S77/69/ComPoint/CBA |  |  |  | CDC | 209 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-31-09 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.69KV_CBF | 69KV斷路器輕故障 | OTHER | S77/69/ComPoint/CBF |  |  |  | CDC | 210 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.RTU_S/L | RTU SUPY/LOCAL | OTHER | S77/0/RTU/RTU_R_L |  |  |  | CDC | 211 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
S77 | 佳里二SS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.TEST_CB | TEST CB | OTHER | S77/0/RTU/Test_CB |  |  |  | CDC | 212 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-30-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.其他輕故障 | 變電所內其他輕故障 | OTHER | S77/0/StaDev/PSF |  |  |  | CDC | 213 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-32-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | S77/0/StaDev/ACB1 |  |  |  | CDC | 214 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S77 | 佳里二SS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-32-13 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | S77/0/StaDev/ACB2 |  |  |  | CDC | 215 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
S77 | 佳里二SS | 0 |  |  |  |  | STUV | [17 empty] | 1-30-08 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | S77/0/StaDev/STUV |  |  |  | CDC | 216 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-30-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.直流充電機故障 | 直流充電機故障 | OTHER | S77/0/StaDev/CHG1 |  |  |  | CDC | 217 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | DCA | [17 empty] | 1-30-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.直流電源DCA | 直流NFB跳脫監視 | OTHER | S77/0/StaDev/DCA |  |  |  | CDC | 218 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | DCE | [17 empty] | 1-30-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.直流電源DCE | 直流電源接地故障警報 | OTHER | S77/0/StaDev/DCE |  |  |  | CDC | 219 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-30-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.洩油池水位警報 | 洩油池水位警報 | OTHER | S77/0/StaDev/OilLeak |  |  |  | CDC | 220 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | SUBA | [17 empty] | 1-37-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.通訊OLTE重故障 | 通訊設備OLTE重故障 | OTHER | S77/0/StaDev/5A5Other |  |  |  | CDC | 221 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | SUBF | [17 empty] | 1-37-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.通訊OLTE輕故障 | 通訊設備OLTE輕故障 | OTHER | S77/0/StaDev/6A5Other |  |  |  | CDC | 222 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-37-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.通訊PCM警報 | 通訊設備PCM警報 | OTHER | S77/0/StaDev/7A5Other |  |  |  | CDC | 223 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-30-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.通訊充電機故障 | 通訊充電機故障 | OTHER | S77/0/StaDev/CHG2 |  |  |  | CDC | 224 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | S77/0/StaDev/CommACF |  |  |  | CDC | 225 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | Door1 | [17 empty] | 1-31-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.無人化門禁(1) | 無人化門禁(1) | OTHER | S77/0/StaDev/Door1 |  |  |  | CDC | 226 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
S77 | 佳里二SS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-30-06 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.開關場照明(A) | 所內開關場路燈照明 | OTHER | S77/0/StaDev/Lights1 |  |  |  | CDC | 227 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
S77 | 佳里二SS | 0 |  |  |  |  | 69KVSC警報 | [17 empty] | 1-31-08 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.69KVSC警報 | 69KVSC警報 | OTHER |  |  |  |  | CDC | 228 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | RTU | RTU |  | DC故障 | [17 empty] | 1-32-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.RTU_DC故障 | RTU DC故障 | OTHER | S77/0/RTU/DCA |  |  |  | CDC | 229 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 水氣霧故障 | [17 empty] | 1-31-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.水氣霧故障 | 水氣霧故障 | OTHER | S77/0/StaDev/2A5Other |  |  |  | CDC | 230 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 水氣霧警報 | [17 empty] | 1-31-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.水氣霧警報 | 水氣霧警報 | OTHER | S77/0/StaDev/3A5Other |  |  |  | CDC | 231 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | Fire | [17 empty] | 1-30-10 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.火災警報 | 火警 | OTHER | S77/0/StaDev/Fire |  |  |  | CDC | 232 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 安全監控 | [17 empty] | 1-30-11 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.安全監控 | 安全監控 | OTHER | S77/0/StaDev/1A5Other |  |  |  | CDC | 233 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 門禁小門 | [17 empty] | 1-30-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.門禁小門 | 門禁小門 | OTHER | S77/0/StaDev/Door2 |  |  |  | CDC | 234 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/ALARM | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 開關場照明A/M | [17 empty] | 1-30-07 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.開關場照明A/M | 開關場照明自動手動 | OTHER | S77/0/StaDev/Lights |  |  |  | CDC | 235 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
S77 | 佳里二SS | 0 |  | 全所30RY | 全所30RY |  | A/S | [17 empty] | 1-14-05 |  | 1-57 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.全所30RY_A/S | 全所故障指示器動作/復歸 | OTHER | S77/0/StaDev/4A5Other |  |  |  | CDC | 236 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/RESET | RESET
S77 | 佳里二SS | 11 | 11kV | _IED | _IED |  | FA | [17 empty] | 1-31-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.11KV_IED_FA | 11KV IED故障 | OTHER | S77/11/ComPoint/IRFA |  |  |  | CDC | 237 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | _IED | _IED |  | CFA | [17 empty] | 1-31-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.69KV_IED_CFA | 69KV IED通訊故障 | OTHER | S77/69/ComPoint/CFA |  |  |  | CDC | 238 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | _IED | _IED |  | FA | [17 empty] | 1-31-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.69KV_IED_FA | 69KV IED故障 | OTHER | S77/69/ComPoint/IRFA |  |  |  | CDC | 239 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 81RY_IED | 81RY_IED |  | FA | [17 empty] | 1-30-13 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.81RY_IED_FA | 低頻IED故障 | OTHER | S77/0/StaDev/81A_RYFA |  |  |  | CDC | 240 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | PM | PM |  | CFA | [17 empty] | 1-31-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.PM_CFA | PM通訊故障 | OTHER | S77/0/StaDev/PMA |  |  |  | CDC | 241 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 63Q | [17 empty] | 1-18-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_63Q | #6MTR ULTC電驛動作 | OTHER | S77//6MTR/63Q |  |  |  | CDC | 242 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 96B1 | [17 empty] | 1-18-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_96B1 | #6MTR 撲氣電驛警報 | OTHER | S77//6MTR/96B1 |  |  |  | CDC | 243 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 96B2 | [17 empty] | 1-18-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_96B2 | #6MTR 撲氣電驛動作 | OTHER | S77//6MTR/96B2 |  |  |  | CDC | 244 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 96D | [17 empty] | 1-18-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_96D | #6MTR 放壓電驛動作 | OTHER | S77//6MTR/96D |  |  |  | CDC | 245 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 96P | [17 empty] | 1-18-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_96P | #6MTR 突壓電驛動作 | OTHER | S77//6MTR/96P |  |  |  | CDC | 246 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 63Q | [17 empty] | 1-18-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_63Q | #7MTR ULTC電驛動作 | OTHER | S77//7MTR/63Q |  |  |  | CDC | 247 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 96B1 | [17 empty] | 1-19-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_96B1 | #7MTR 撲氣電驛警報 | OTHER | S77//7MTR/96B1 |  |  |  | CDC | 248 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 96B2 | [17 empty] | 1-19-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_96B2 | #7MTR 撲氣電驛動作 | OTHER | S77//7MTR/96B2 |  |  |  | CDC | 249 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 96D | [17 empty] | 1-18-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_96D | #7MTR 放壓電驛動作 | OTHER | S77//7MTR/96D |  |  |  | CDC | 250 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 96P | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_96P | #7MTR 突壓電驛動作 | OTHER | S77//7MTR/96P |  |  |  | CDC | 251 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 變電所低水位 | [17 empty] | 1-30-09 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.變電所低水位 | 變電所低水位 | OTHER | S77/0/StaDev/Water1 |  |  |  | CDC | 252 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  |  |  |  | 變電所高水位 | [17 empty] | 1-31-06 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.變電所高水位 | 變電所高水位 | OTHER | S77/0/StaDev/Water2 |  |  |  | CDC | 253 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN11 | 佳安線 |  | LOA | [17 empty] | 1-3F-01 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_LOA | 佳安線 復閉失敗閉鎖 | OTHER | S77/11/KN11/LOA |  |  |  | CDC | 254 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN12 | 佳華線 |  | LOA | [17 empty] | 1-3F-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_LOA | 佳華線 復閉失敗閉鎖 | OTHER | S77/11/KN12/LOA |  |  |  | CDC | 255 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN13 | 佳洲線 |  | LOA | [17 empty] | 1-3F-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_LOA | 佳洲線 復閉失敗閉鎖 | OTHER | S77/11/KN13/LOA |  |  |  | CDC | 256 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN14 | 佳14線 |  | LOA | [17 empty] | 1-3F-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_LOA | 佳14線 復閉失敗閉鎖 | OTHER | S77/11/KN14/LOA |  |  |  | CDC | 257 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN15 | 佳15線 |  | LOA | [17 empty] | 1-3F-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_LOA | 佳15線 復閉失敗閉鎖 | OTHER | S77/11/KN15/LOA |  |  |  | CDC | 258 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN16 | 佳16線 |  | LOA | [17 empty] | 1-3F-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_LOA | 佳16線 復閉失敗閉鎖 | OTHER | S77/11/KN16/LOA |  |  |  | CDC | 259 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN17 | 佳坪線 |  | LOA | [17 empty] | 1-3E-15 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_LOA | 佳坪線 復閉失敗閉鎖 | OTHER | S77/11/KN17/LOA |  |  |  | CDC | 260 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN18 | 佳頂線 |  | LOA | [17 empty] | 1-3E-14 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_LOA | 佳頂線 復閉失敗閉鎖 | OTHER | S77/11/KN18/LOA |  |  |  | CDC | 261 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN19 | 佳農線 |  | LOA | [17 empty] | 1-3E-13 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_LOA | 佳農線 復閉失敗閉鎖 | OTHER | S77/11/KN19/LOA |  |  |  | CDC | 262 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | KN20 | 佳20線 |  | LOA | [17 empty] | 1-3E-12 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_LOA | 佳20線 復閉失敗閉鎖 | OTHER | S77/11/KN20/LOA |  |  |  | CDC | 263 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 6_MAIN | #6MCB |  | 51NA | [17 empty] | 1-01-00 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6_MAIN_51NA | #6MCB GDA | OTHER | S77/11/M6/51NA |  |  |  | CDC | 264 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7_MAIN | #7MCB |  | 51NA | [17 empty] | 1-02-02 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7_MAIN_51NA | #7MCB GDA | OTHER | S77/11/M7/51NA |  |  |  | CDC | 265 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | DS1 | 861 | [16 empty] | 1-38-08 | 1-38-09 | 1-24 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.861_DS | 861(#6MTR) DS | DTR | S77/69/860/DS1 |  |  |  | CDC | 266 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | DS2 | 862 | [16 empty] | 1-38-10 | 1-38-11 | 1-25 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.862_DS | 862(#6MTR) DS | DTR | S77/69/860/DS2 |  |  |  | CDC | 267 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S77 | 佳里二SS | 0 |  | 6MTR | #6MTR |  | 96PA | [17 empty] | 1-00-05 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#6MTR_96PA | #6MTR 機械保護動作 | DTR | S77//6MTR/96PA |  |  |  | CDC | 268 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 0 |  | 7MTR | #7MTR |  | 96PA | [17 empty] | 1-01-07 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.#7MTR_96PA | #7MTR 機械保護動作 | DTR | S77//7MTR/96PA |  |  |  | CDC | 269 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | DS1 | 871 | [16 empty] | 1-38-12 | 1-38-13 | 1-26 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.871_DS | 871(#7MTR) DS | DTR | S77/69/870/DS1 |  |  |  | CDC | 270 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | DS2 | 872 | [16 empty] | 1-38-14 | 1-38-15 | 1-27 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.872_DS | 872(#7MTR) DS | DTR | S77/69/870/DS2 |  |  |  | CDC | 271 | GENERICDIPoint | SS419_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
S77 | 佳里二SS | 11 | 11kV | TIE6 | #7-#6 |  | CB | [17 empty] | 1-0C-05 |  | 1-32 | [5 empty] | DDCS4_2 | [8 empty] | 佳二SS.TIE6_CB | 11KV #7-#6 TIE CB | TIE | S77/11/TIE6/CB |  |  |  | CDC | 272 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 11 | 11kV | TIE6 | #7-#6 |  | 51A | [17 empty] | 1-0E-03 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.TIE6_51A | 11KV #7-#6 TIE 51RY | TIE | S77/11/TIE6/51A |  |  |  | CDC | 273 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | TIE6 | #7-#6 |  | 51NA | [17 empty] | 1-0E-04 | [7 empty] | DDCS4_2 | [8 empty] | 佳二SS.TIE6_51NA | 11KV #7-#6 TIE 51N RY | TIE | S77/11/TIE6/51NA |  |  |  | CDC | 274 | GENERICDIPoint | SS419_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
S77 | 佳里二SS | 11 | 11kV | 260_SC | #6SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_SC_CAP | 11KV#6SC 容量 | SC | S77/11/260/1AI_Oth |  |  |  |  | 275 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 11 | 11kV | 270_SC | #7SC | 6 | CAP | [25 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_SC_CAP | 11KV#7SC 容量 | SC | S77/11/270/2AI_Oth |  |  |  |  | 276 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
S77 | 佳里二SS | 0 |  | KN11 | KN11_DS |  | DS1 | KN11_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_DS | KN11_DS (非取樣點) | FEEDER | S77/11/KN11/DS |  |  |  |  | 277 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN11 | KN11_ES |  | LE0 | KN11_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN11_ES | KN11_ES (非取樣點) | FEEDER | S77/11/KN11/ES |  |  |  |  | 278 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN12 | KN12_DS |  | DS1 | KN12_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_DS | KN12_DS (非取樣點) | FEEDER | S77/11/KN12/DS |  |  |  |  | 279 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN12 | KN12_ES |  | LE0 | KN12_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN12_ES | KN12_ES (非取樣點) | FEEDER | S77/11/KN12/ES |  |  |  |  | 280 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN13 | KN13_DS |  | DS1 | KN13_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_DS | KN13_DS (非取樣點) | FEEDER | S77/11/KN13/DS |  |  |  |  | 281 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN13 | KN13_ES |  | LE0 | KN13_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN13_ES | KN13_ES (非取樣點) | FEEDER | S77/11/KN13/ES |  |  |  |  | 282 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN14 | KN14_DS |  | DS1 | KN14_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_DS | KN14_DS (非取樣點) | FEEDER | S77/11/KN14/DS |  |  |  |  | 283 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN14 | KN14_ES |  | LE0 | KN14_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN14_ES | KN14_ES (非取樣點) | FEEDER | S77/11/KN14/ES |  |  |  |  | 284 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN15 | KN15_DS |  | DS1 | KN15_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_DS | KN15_DS (非取樣點) | FEEDER | S77/11/KN15/DS |  |  |  |  | 285 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN15 | KN15_ES |  | LE0 | KN15_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN15_ES | KN15_ES (非取樣點) | FEEDER | S77/11/KN15/ES |  |  |  |  | 286 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN16 | KN16_DS |  | DS1 | KN16_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_DS | KN16_DS (非取樣點) | FEEDER | S77/11/KN16/DS |  |  |  |  | 287 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN16 | KN16_ES |  | LE0 | KN16_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN16_ES | KN16_ES (非取樣點) | FEEDER | S77/11/KN16/ES |  |  |  |  | 288 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN17 | KN17_DS |  | DS1 | KN17_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_DS | KN17_DS (非取樣點) | FEEDER | S77/11/KN17/DS |  |  |  |  | 289 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN17 | KN17_ES |  | LE0 | KN17_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN17_ES | KN17_ES (非取樣點) | FEEDER | S77/11/KN17/ES |  |  |  |  | 290 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN18 | KN18_DS |  | DS1 | KN18_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_DS | KN18_DS (非取樣點) | FEEDER | S77/11/KN18/DS |  |  |  |  | 291 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN18 | KN18_ES |  | LE0 | KN18_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN18_ES | KN18_ES (非取樣點) | FEEDER | S77/11/KN18/ES |  |  |  |  | 292 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN19 | KN19_DS |  | DS1 | KN19_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_DS | KN19_DS (非取樣點) | FEEDER | S77/11/KN19/DS |  |  |  |  | 293 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN19 | KN19_ES |  | LE0 | KN19_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN19_ES | KN19_ES (非取樣點) | FEEDER | S77/11/KN19/ES |  |  |  |  | 294 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | KN20 | KN20_DS |  | DS1 | KN20_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_DS | KN20_DS (非取樣點) | FEEDER | S77/11/KN20/DS |  |  |  |  | 295 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | KN20 | KN20_ES |  | LE0 | KN20_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.KN20_ES | KN20_ES (非取樣點) | FEEDER | S77/11/KN20/ES |  |  |  |  | 296 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | 6M | 6M_DS |  | DS1 | 6M_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.6M_DS | 6M_DS (非取樣點) | DTR | S77/11/M6/DS |  |  |  |  | 297 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 6M | 6M_ES |  | M0 | 6M_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.6M_ES | 6M_ES (非取樣點) | DTR | S77/11/M6/ES |  |  |  |  | 298 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | 7M | 7M_DS |  | DS1 | 7M_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.7M_DS | 7M_DS (非取樣點) | DTR | S77/11/M7/DS |  |  |  |  | 299 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 7M | 7M_ES |  | M0 | 7M_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.7M_ES | 7M_ES (非取樣點) | DTR | S77/11/M7/ES |  |  |  |  | 300 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_ES | 260_ES (非取樣點) | SC | S77/11/260/ES |  |  |  |  | 301 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.260_DS | 260_DS (非取樣點) | SC | S77/11/260/DS |  |  |  |  | 302 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 270 | #7SC(270) |  | LE0 | 270_ES | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_ES | 270_ES (非取樣點) | SC | S77/11/270/ES |  |  |  |  | 303 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | 270 | #7SC(270) |  | DS1 | 270_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.270_DS | 270_DS (非取樣點) | SC | S77/11/270/DS |  |  |  |  | 304 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
S77 | 佳里二SS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 佳二SS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 305 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 306 | NotelDIPoint | [38 empty] | START/STOP | STOP
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | TE0 | 860TE | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.860TE | 860TE (非取樣點) | DTR | S77/69/860/TE0 |  |  |  |  | 307 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 69 | 69kV | 860 | #6MTR(860) |  | BE0 | 860BE | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.860BE | 860BE (非取樣點) | DTR | S77/69/860/BE0 |  |  |  |  | 308 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | TE0 | 870TE | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.870TE | 870TE (非取樣點) | DTR | S77/69/870/TE0 |  |  |  |  | 309 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 69 | 69kV | 870 | #7MTR(870) |  | BE0 | 870BE | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.870BE | 870BE (非取樣點) | DTR | S77/69/870/BE0 |  |  |  |  | 310 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
S77 | 佳里二SS | 0 |  | TIE6 | #7-#6 |  | DS1 | TIE6_DS | [24 empty] | DDCS4_2 | [8 empty] | 佳二SS.TIE6_DS | #7-#6 TIE_DS (非取樣點) | TIE | S77/11/TIE6/D1 |  |  |  |  | 311 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo